## Hardy Cross
1
| Pipes. Network analysis using the Hardy Cross method _Imperial units | [5 empty] | [3]
The water system shown in Figure 1 has the folowing data:
| Table 1 | [5 empty] | Table 2 | [5 empty] | Table 3
|  | Junctions coordinates (ft) |  |  |  |  | Total number of houses in the system
| Node | x-coord. | y-coord | z-coord |  |  | (named as number of units Nu) | [5 empty] | Pipe diameters, Hazen-Williams constant
Reservoir | A | -100 | 1200 | 250 |  |  | Nu = | 300 | - |  |  |  | and length are given in Table 3
1 | D | 1500 | 1200 | 100
2 | E | 1500 | 800 | 80 |  |  | Average day unit demnad | [5 empty] | Pipe ID | D (in) | C | L (ft)
3 | F | 1500 | 0 | 135 |  |  | q = | 1140 | gpd/unit |  |  |  | JD | 8 | 130 | 1500
4 | G | 750 | 0 | 80 | [8 empty] | DE | 8 | 130 | 400
5 | H | 0 | 0 | 140 |  |  | Nº of junctions | [5 empty] | EK | 8 | 130 | 750
6 | I | 0 | 800 | 80 |  |  | Nj = | 8 | - |  |  |  | KI | 8 | 130 | 750
7 | J | 0 | 1200 | 120 | [8 empty] | IJ | 8 | 130 | 400
8 | K | 750 | 800 | 145 |  |  | Max Day Factor
[7 empty] | MDF = | 1.75 | - |  |  |  | IK | 8 | 130 | 750
[13 empty] | KG | 8 | 130 | 800
[7 empty] | Fire flow | [5 empty] | GH | 8 | 130 | 750
[7 empty] | FF = | 1750 | gpm |  |  |  | HI | 8 | 130 | 800
[13 empty] | KE | 8 | 130 | 750
[13 empty] | EF | 8 | 130 | 800
[13 empty] | FG | 8 | 130 | 750
[13 empty] | GK | 8 | 130 | 800
[13 empty] | AJ | 8 | 130 | 100
Note. Length can be obtained from Table 2
2
1.- Assign flow directions in the loops
2.- Water demand in each junction
A clockweise direction is assigned as positive | [16 empty] | 4.- Assing flow values to the map
[6 empty] | In the example the demands are defined |  |  |  |  | 3.- Assign the fire flow to junction F | [5 empty] | With data from Table 4
[6 empty] | as follows |  |  |  |  | Fire Flow
[11 empty] | FF = | 1750 | gpm |  |  | Source A
[6 empty] | Average day demand in the system | [10 empty] | J | 51.9531 |  |  |  |  | 51.9531 | D
[6 empty] | AD = | Nu* q
[6 empty] | NU = | 300 | units |  |  | Consumption at the nodes
[6 empty] | q = | 1140 | gpd/unit |  |  | Table 4
[6 empty] | AD = | 342000 | gpd/system |  |  | Consumptions in nodes
[11 empty] | Qj = | DpJ = | 51.9531 | gpm |  |  | I |  |  | K |  |  |  | E
[6 empty] | Ave minute demand |  |  |  |  | Qd = | DpJ = | 51.9531 | gpm |  |  |  | 51.9531 |  |  | 51.9531 |  | 51.9531
[6 empty] | AmD = | AD / (24*60) |  |  |  | Qi = | DpJ = | 51.9531 | gpm
[6 empty] | AmD = | 237.5 | gpm/system |  |  | Qk = | DpJ = | 51.9531 | gpm
[11 empty] | Qe = | DpJ = | 51.9531 | gpm
[6 empty] | Max day demand |  |  |  |  | Qh = | DpJ = | 51.9531 | gpm
[6 empty] | MDD = | AmD * MDF |  |  |  | Qg = | DpJ = | 51.9531 | gpm
[6 empty] | AmD = | 237.5 |  |  |  | Qf = | DPj + FF | 1801.9531 | gpm |  | Source C | H | 51.9531 |  | G | 51.9531 |  | 1801.9531 | F
[6 empty] | MDF = | 1.75
[6 empty] | MDD = | 415.625 | gpm/system |  |  | System demand
[11 empty] | SD = | MDD + FF | [7 empty] | Figure 3
[6 empty] | Assuming that all junction demans are |  |  |  |  | MDD = | 415.625 | gpm/system
[6 empty] | the same |  |  |  |  | FF = | 1750 | gpm
[6 empty] | Demand per Junction |  |  |  |  | SD = | 2165.625 | gpm
[6 empty] | DpJ = | MDD / Nj
[6 empty] | MDD = | 415.625 | gpm/system
[6 empty] | Nj = | 8
[6 empty] | DpJ = | 51.9531 | gpm/junction
3
5,. Asign flow rates and flow directions to the pipes
[11 empty] | Source A | 2113.6719 |  |  | 103.9062
Table 5 | [11 empty] | J | 51.9531 |  |  |  |  | 51.9531 | D
Assigned flows and calculated | [11 empty] | 2009.7656
values | [18 empty] | 51.9531
Let
Qgf = | QF/2 |  |  | Qke + Qde = Qe + Qef |  |  | Qik = | Qk + Qkg + Qke |  |  |  | I |  | 1002.9297 | K |  | 900.9766 |  | E
Qf = | 1801.9531 | gpm |  | Qde = | Qe + Qef - Qke |  | Qk = | 51.9531 |  |  |  |  | 51.9531 |  |  | 51.9531 |  | 51.9531
Qgf = | 900.9766 | gpm |  | Qe = | 51.9531 |  | Qkg = | 50
|  |  |  | Qef = | 900.9766 |  | Qke = | 900.9766 |  |  |  | 954.8828 |  |  |  | 50
then |  |  |  | Qke = | 900.9766 |  | Qik = | 1002.9297 | gpm | [9 empty] | 900.9766
Qef = | Qf - Qgf |  |  | Qde = | 51.9531 | gpm
Qf = | 1801.9531 | [5 empty] | Qih = | Qh + Qhg
Qgf = | 900.9766 |  |  | Qjd = | Qd+Qde |  | Qh = | 51.9531 |  |  | Source C | H | 51.9531 |  | G | 51.9531 |  | 1801.9531 | F
Qef = | 900.9766 | gpm |  | Qd = | 51.9531 |  | Qhg = | 902.9297 | [5 empty] | 902.9297 |  |  | 900.9766
|  |  |  | Qde = | 51.9531 |  | Qih = | 954.8828 | gpm
Let |  |  |  | Qjd = | 103.9062 | gpm | [7 empty] | Figure 4
Qke = | Qef | [5 empty] | Qji = | Qi + Qih + Qik
Qke = | 900.9766 | gpm |  | QHg + Qkg = Qg + Qgf |  |  | Qi = | 51.9531
|  |  |  | QHg = | Qg + Qgf - Qkg |  | Qih = | 954.8828
Let |  |  |  | Qg = | 51.9531 |  | Qik = | 1002.9297
Qkg = | 50 | gpm |  | Qgf = | 900.9766 |  | Qji = | 2009.7656 | gpm
|  |  |  | Qkg = | 50
FF = | 1750 | gpm |  | QHg = | 902.9297 | gpm | QAJ = | Qji + QJD
[7 empty] | QJI = | 2009.7656
[7 empty] | Q JD = | 103.9062
[7 empty] | QAJ = | 2113.6719 | gpm
4
6.- Tabulate flows obtained in Table 5 |  |  |  |  | 7.- Assign signs of flows, according Figure 4
[15 empty] | Source A | 0 |  |  | 103.9062
[6 empty] | Input information for the pipe running from thr reservoir to the first | [9 empty] | J | 51.9531 |  |  |  |  | 51.9531 | D
system junction
[6 empty] | Pipe ID | D (in) | C | L (ft) | r | Q (gpm) | h (ft) |  |  |  | 2009.7656
[6 empty] | A-J | 8 | 130 | 100 | 5.1466e-06 | 2113.6719 | 7.2918 | [10 empty] | 51.9531
[10 empty] | (Eq.1) | Note 1
Table 6 |  |  |  |  | Table 6 | [10 empty] | I |  | 1002.9297 | K |  | 900.9766 |  | E
[17 empty] | 0 |  |  | 0 |  | 0
| Pipe ID | Q (gpm) |  |  |  | Pipe ID | D (in) | C | L (ft) | r | Q (gpm) | h (ft)
|  | Note 1 | [8 empty] | Note 1 |  |  |  |  | 954.8828 |  |  |  | 50
| JD | 103.9062 |  |  |  | JD | 8 | 130 | 1500 |  | 103.9062 | [11 empty] | 900.9766
Loop | DE | 51.9531 |  |  | Loop | DE | 8 | 130 | 400 |  | 51.9531
JDEKI | EK | 900.9766 |  |  | JDEKI | EK | 8 | 130 | 750 |  | -900.9766
| KI | 1002.9297 |  |  |  | KI | 8 | 130 | 750 |  | -1002.9297 |  |  |  | Source C | H | 0 |  | G | 0 |  | 0 | F
| IJ | 2009.7656 |  |  |  | IJ | 8 | 130 | 400 |  | -2009.7656 | [6 empty] | 902.9297 |  |  | 900.9766
| IK | 1002.9297 |  |  |  | IK | 8 | 130 | 750 |  | 1002.9297 | [6 empty] | Figure 4 (repeated)
Loop | KG | 50 |  |  | Loop | KG | 8 | 130 | 800 |  | 50
IKGH | GH | 902.9297 |  |  | IKGH | GH | 8 | 130 | 750 |  | -902.9297
| HI | 954.8828 |  |  |  | HI | 8 | 130 | 800 |  | -954.8828
| KE | 900.9766 |  |  |  | KE | 8 | 130 | 750 |  | 900.9766
Loop | EF | 900.9766 |  |  | Loop | EF | 8 | 130 | 800 |  | 900.9766
KEFG | FG | 900.9766 |  |  | KEFG | FG | 8 | 130 | 750 |  | -900.9766
| GK | 50 |  |  |  | GK | 8 | 130 | 800 |  | -50
| AJ | 2113.6719 |  |  |  | AJ | 8 | 130 | 100
Note 1. | From Table 5
5
8.- Equations of Hardy Cross methos (imperial units)
6
9.- Iterations. Table 4
[5 empty] | Modification of (Eq.2) to allow for a | [12 empty] | n = | 1.85 |  | Shared pipes
[5 empty] | a copy-paste method for the next | [15 empty] | For example, shared pipes shown in green cells
[5 empty] | iterations (shared pipes). | [15 empty] | In this case, the adjusted flow will be
[5 empty] | IF(Q<0,-h*ABS(Q)^1.85,$r*ABS(Q)^1.85) | [15 empty] | Qajd(EK) = | Qini(EK) + DQ(EK) - DQ(KE)
Input information for the pipe running from thr reservoir to the first system junction
| Pipe ID | D (in) | C | L (ft) | r | Q (gpm) | h (ft) | R
[5 empty] | (Eq.1) |  | (Eq.2) | (Eq.3)
| A-J | 8 | 130 | 100 | 5.1466e-06 | 2113.6719 | 7.2918 | 0.0063822
| 1 | iteration | [7 empty] | 2 | iteration |  |  | 3 | iteration |  |  | 4 | iteration |  |  | 5 | iteration |  |  | 6 | iteration |  |  | 7 | iteration |  |  | 8 | iteration |  |  | 9 | iteration |  |  | 10 | iteration |  |  | 11 | iteration |  |  | 12 | iteration
| Pipe ID | D (in) | C | L (ft) | r | Q (gpm) | h (ft) | R | DQ (gpm) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs) | Qadj | h (ft) | R | DQ (cfs)
[5 empty] | (Eq.1) |  | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3) |  | (Eq.5) | (Eq.2) | (Eq.3)
| JD | 8 | 130 | 1500 | 7.7199e-05 | 103.9062 | 0.41533 | 0.0073948 | 627.7944 | 731.7006 | 15.3683 | 0.038857 | -16.2654 | 715.4352 | 14.7423 | 0.038121 | 41.7534 | 757.1886 | 16.3733 | 0.040004 | 6.7243 | 763.9129 | 16.6433 | 0.040306 | 4.078 | 767.9909 | 16.8081 | 0.040489 | 1.0741 | 769.0651 | 16.8516 | 0.040537 | 0.48234 | 769.5474 | 16.8711 | 0.040558 | 0.14797 | 769.6954 | 16.8771 | 0.040565 | 0.059673 | 769.755 | 16.8796 | 0.040568 | 0.019676 | 769.7747 | 16.8804 | 0.040569 | 0.0075191 | 769.7822 | 16.8807 | 0.040569 | 0.0025766
Loop | DE | 8 | 130 | 400 | 2.0586e-05 | 51.9531 | 0.030723 | 0.001094 | 627.7944 | 679.7475 | 3.5762 | 0.009733 | -16.2654 | 663.4821 | 3.4195 | 0.0095346 | 41.7534 | 705.2355 | 3.8282 | 0.010042 | 6.7243 | 711.9598 | 3.896 | 0.010124 | 4.078 | 716.0378 | 3.9374 | 0.010173 | 1.0741 | 717.1119 | 3.9483 | 0.010186 | 0.48234 | 717.5943 | 3.9532 | 0.010192 | 0.14797 | 717.7422 | 3.9548 | 0.010193 | 0.059673 | 717.8019 | 3.9554 | 0.010194 | 0.019676 | 717.8216 | 3.9556 | 0.010194 | 0.0075191 | 717.8291 | 3.9556 | 0.010195 | 0.0025766
JDEKI | EK | 8 | 130 | 750 | 3.8599e-05 | -900.9766 | -11.2927 | 0.023188 | 627.7944 | -109.4669 | -0.22869 | 0.0038649 | -16.2654 | -269.3374 | -1.2096 | 0.0083081 | 41.7534 | -250.0248 | -1.054 | 0.007799 | 6.7243 | -252.8258 | -1.076 | 0.0078732 | 4.078 | -252.5151 | -1.0735 | 0.0078649 | 1.0741 | -252.6108 | -1.0743 | 0.0078675 | 0.48234 | -252.6049 | -1.0742 | 0.0078673 | 0.14797 | -252.6119 | -1.0743 | 0.0078675 | 0.059673 | -252.6121 | -1.0743 | 0.0078675 | 0.019676 | -252.6128 | -1.0743 | 0.0078675 | 0.0075191 | -252.6129 | -1.0743 | 0.0078675 | 0.0025766
| KI | 8 | 130 | 750 | 3.8599e-05 | -1002.9297 | -13.7699 | 0.0254 | 627.7944 | -517.4926 | -4.0486 | 0.014473 | -16.2654 | -708.9908 | -7.2488 | 0.018915 | 41.7534 | -692.4761 | -6.9395 | 0.018539 | 6.7243 | -702.5216 | -7.1269 | 0.018768 | 4.078 | -702.3024 | -7.1228 | 0.018763 | 1.0741 | -703.1747 | -7.1391 | 0.018783 | 0.48234 | -703.2397 | -7.1404 | 0.018784 | 0.14797 | -703.328 | -7.142 | 0.018786 | 0.059673 | -703.3425 | -7.1423 | 0.018786 | 0.019676 | -703.3523 | -7.1425 | 0.018787 | 0.0075191 | -703.3546 | -7.1425 | 0.018787 | 0.0025766
| IJ | 8 | 130 | 400 | 2.0586e-05 | -2009.7656 | -26.5703 | 0.024458 | 627.7944 | -1381.9712 | -13.2893 | 0.01779 | -16.2654 | -1398.2366 | -13.5801 | 0.017968 | 41.7534 | -1356.4832 | -12.8394 | 0.017511 | 6.7243 | -1349.7589 | -12.7219 | 0.017437 | 4.078 | -1345.681 | -12.6509 | 0.017392 | 1.0741 | -1344.6068 | -12.6322 | 0.01738 | 0.48234 | -1344.1245 | -12.6238 | 0.017375 | 0.14797 | -1343.9765 | -12.6213 | 0.017373 | 0.059673 | -1343.9168 | -12.6202 | 0.017373 | 0.019676 | -1343.8972 | -12.6199 | 0.017372 | 0.0075191 | -1343.8896 | -12.6197 | 0.017372 | 0.0025766
[6 empty] | Sum | -51.1869 | 0.081534 |  | Sum | 1.378 | 0.084718 |  | Sum | -3.8766 | 0.092846 |  | Sum | -0.63138 | 0.093895 |  | Sum | -0.3854 | 0.094507 |  | Sum | -0.1017 | 0.094681 |  | Sum | -0.045703 | 0.094753 |  | Sum | -0.014024 | 0.094776 |  | Sum | -0.0056561 | 0.094785 |  | Sum | -0.0018651 | 0.094788 |  | Sum | -0.00071273 | 0.09479 |  | Sum | -0.00024424 | 0.09479
| IK | 8 | 130 | 750 | 3.8599e-05 | 1002.9297 | 13.7699 | 0.0254 | 142.3573 | 517.4926 | 4.0486 | 0.014473 | 175.2328 | 708.9908 | 7.2488 | 0.018915 | 25.2388 | 692.4761 | 6.9395 | 0.018539 | 16.7698 | 702.5216 | 7.1269 | 0.018768 | 3.8588 | 702.3024 | 7.1228 | 0.018763 | 1.9464 | 703.1747 | 7.1391 | 0.018783 | 0.54736 | 703.2397 | 7.1404 | 0.018784 | 0.23625 | 703.328 | 7.142 | 0.018786 | 0.074187 | 703.3425 | 7.1423 | 0.018786 | 0.029419 | 703.3523 | 7.1425 | 0.018787 | 0.0098147 | 703.3546 | 7.1425 | 0.018787 | 0.003718
Loop | KG | 8 | 130 | 800 | 4.1173e-05 | 50 | 0.05724 | 0.0021179 | 142.3573 | 356.0725 | 2.1625 | 0.011235 | 175.2328 | 387.7003 | 2.5312 | 0.012078 | 25.2388 | 390.4982 | 2.5651 | 0.012152 | 16.7698 | 397.7427 | 2.6538 | 0.012344 | 3.8588 | 397.8342 | 2.655 | 0.012346 | 1.9464 | 398.6108 | 2.6645 | 0.012366 | 0.54736 | 398.6817 | 2.6654 | 0.012368 | 0.23625 | 398.763 | 2.6664 | 0.01237 | 0.074187 | 398.7773 | 2.6666 | 0.012371 | 0.029419 | 398.7864 | 2.6667 | 0.012371 | 0.0098147 | 398.7886 | 2.6667 | 0.012371 | 0.003718
IKGH | GH | 8 | 130 | 750 | 3.8599e-05 | -902.9297 | -11.3381 | 0.02323 | 142.3573 | -760.5724 | -8.2545 | 0.020078 | 175.2328 | -585.3396 | -5.0849 | 0.016071 | 25.2388 | -560.1008 | -4.6867 | 0.01548 | 16.7698 | -543.331 | -4.4305 | 0.015085 | 3.8588 | -539.4723 | -4.3724 | 0.014994 | 1.9464 | -537.5259 | -4.3433 | 0.014948 | 0.54736 | -536.9785 | -4.3351 | 0.014935 | 0.23625 | -536.7422 | -4.3316 | 0.01493 | 0.074187 | -536.6681 | -4.3305 | 0.014928 | 0.029419 | -536.6386 | -4.33 | 0.014927 | 0.0098147 | -536.6288 | -4.3299 | 0.014927 | 0.003718
| HI | 8 | 130 | 800 | 4.1173e-05 | -954.8828 | -13.4127 | 0.025986 | 142.3573 | -812.5255 | -9.9496 | 0.022654 | 175.2328 | -637.2927 | -6.348 | 0.018428 | 25.2388 | -612.054 | -5.8907 | 0.017805 | 16.7698 | -595.2842 | -5.5956 | 0.01739 | 3.8588 | -591.4254 | -5.5287 | 0.017294 | 1.9464 | -589.479 | -5.4951 | 0.017246 | 0.54736 | -588.9316 | -5.4856 | 0.017232 | 0.23625 | -588.6954 | -5.4816 | 0.017226 | 0.074187 | -588.6212 | -5.4803 | 0.017224 | 0.029419 | -588.5918 | -5.4798 | 0.017224 | 0.0098147 | -588.582 | -5.4796 | 0.017223 | 0.003718
[6 empty] | Sum | -10.9236 | 0.076734 | 142.3573 | Sum | -11.993 | 0.068441 |  | Sum | -1.6529 | 0.065491 |  | Sum | -1.0729 | 0.063977 |  | Sum | -0.24537 | 0.063586 |  | Sum | -0.1234 | 0.063397 |  | Sum | -0.034671 | 0.063343 |  | Sum | -0.014959 | 0.06332 |  | Sum | -0.004697 | 0.063312 |  | Sum | -0.0018625 | 0.063309 |  | Sum | -0.00062135 | 0.063308 |  | Sum | -0.00023538 | 0.063308
| KE | 8 | 130 | 750 | 3.8599e-05 | 900.9766 | 11.2927 | 0.023188 | -163.7153 | 109.4669 | 0.22869 | 0.0038649 | 143.605 | 269.3374 | 1.2096 | 0.0083081 | 22.4409 | 250.0248 | 1.054 | 0.007799 | 9.5253 | 252.8258 | 1.076 | 0.0078732 | 3.7673 | 252.5151 | 1.0735 | 0.0078649 | 1.1698 | 252.6108 | 1.0743 | 0.0078675 | 0.47647 | 252.6049 | 1.0742 | 0.0078673 | 0.15494 | 252.6119 | 1.0743 | 0.0078675 | 0.059929 | 252.6121 | 1.0743 | 0.0078675 | 0.020345 | 252.6128 | 1.0743 | 0.0078675 | 0.007608 | 252.6129 | 1.0743 | 0.0078675 | 0.0026484
Loop | EF | 8 | 130 | 800 | 4.1173e-05 | 900.9766 | 12.0456 | 0.024734 | -163.7153 | 737.2613 | 8.312 | 0.020857 | 143.605 | 880.8663 | 11.5529 | 0.024263 | 22.4409 | 903.3072 | 12.1033 | 0.024788 | 9.5253 | 912.8325 | 12.3405 | 0.02501 | 3.7673 | 916.5998 | 12.4348 | 0.025098 | 1.1698 | 917.7696 | 12.4642 | 0.025125 | 0.47647 | 918.246 | 12.4762 | 0.025136 | 0.15494 | 918.401 | 12.4801 | 0.02514 | 0.059929 | 918.4609 | 12.4816 | 0.025141 | 0.020345 | 918.4812 | 12.4821 | 0.025141 | 0.007608 | 918.4889 | 12.4823 | 0.025142 | 0.0026484
KEFG | FG | 8 | 130 | 750 | 3.8599e-05 | -900.9766 | -11.2927 | 0.023188 | -163.7153 | -1064.6918 | -15.3795 | 0.026723 | 143.605 | -921.0868 | -11.7635 | 0.023627 | 22.4409 | -898.6459 | -11.2388 | 0.023137 | 9.5253 | -889.1206 | -11.0194 | 0.022928 | 3.7673 | -885.3534 | -10.9331 | 0.022845 | 1.1698 | -884.1836 | -10.9064 | 0.02282 | 0.47647 | -883.7071 | -10.8956 | 0.022809 | 0.15494 | -883.5522 | -10.892 | 0.022806 | 0.059929 | -883.4922 | -10.8907 | 0.022805 | 0.020345 | -883.4719 | -10.8902 | 0.022804 | 0.007608 | -883.4643 | -10.89 | 0.022804 | 0.0026484
| GK | 8 | 130 | 800 | 4.1173e-05 | -50 | -0.05724 | 0.0021179 | -163.7153 | -356.0725 | -2.1625 | 0.011235 | 143.605 | -387.7003 | -2.5312 | 0.012078 | 22.4409 | -390.4982 | -2.5651 | 0.012152 | 9.5253 | -397.7427 | -2.6538 | 0.012344 | 3.7673 | -397.8342 | -2.655 | 0.012346 | 1.1698 | -398.6108 | -2.6645 | 0.012366 | 0.47647 | -398.6817 | -2.6654 | 0.012368 | 0.15494 | -398.763 | -2.6664 | 0.01237 | 0.059929 | -398.7773 | -2.6666 | 0.012371 | 0.020345 | -398.7864 | -2.6667 | 0.012371 | 0.007608 | -398.7886 | -2.6667 | 0.012371 | 0.0026484
[6 empty] | Sum | 11.9883 | 0.073227 |  | Sum | -9.0013 | 0.062681 |  | Sum | -1.5322 | 0.068277 |  | Sum | -0.64654 | 0.067876 |  | Sum | -0.25676 | 0.068155 |  | Sum | -0.079727 | 0.068154 |  | Sum | -0.032485 | 0.068179 |  | Sum | -0.010564 | 0.068181 |  | Sum | -0.0040862 | 0.068183 |  | Sum | -0.0013872 | 0.068184 |  | Sum | -0.00051874 | 0.068184 |  | Sum | -0.00018058 | 0.068184
7
Pressure loss per 1000 ft | [11 empty] | Residual pressure at the junctions
Table 5 | [11 empty] | Table 6
Pipe ID |  | D (in) | C | L (ft) | r | Q (gpm) | h (ft) |  | hfk | [8 empty] | Pressure losses between node A and
|  |  |  | (Eq.1) |  | (Eq.2) | (Eq.3) |  | ft/(1000ft) |  |  |  |  | Coordinates (ft) |  |  | DEL | the selected node |  |  | Residual pressure
A-J | A-J | 8 | 130 | 100 | 5.1466e-06 | 2113.6719 | 7.2918 |  | 72.9184 |  |  |  | Node i | x-coord. | y-coord | z-coord | ELA - ELi |  |  | DP | Presidual = DEL - DP
[14 empty] | ft | ft | ft | ft |  |  | ft | ft | psi
| 1 | iteration |  |  | 12 | iteration | [5 empty] | Reservoir | A | -100 | 1200 | 250 |  | AJ |  | 7.2918
| Pipe ID | D (in) | C | L (ft) | Qadj | h (ft) | R | DQ (cfs) | hfk |  |  |  | D | 1500 | 1200 | 100 | 150 | AD | AJ + JD | 24.1725 | 125.8275 | 54.5416
[5 empty] | (Eq.5) | (Eq.2) | (Eq.3) |  | ft/(1000ft) |  |  |  | E | 1500 | 800 | 80 | 170
| JD | 8 | 130 | 1500 | 769.7822 | 16.8807 | 0.040569 | 0.0025766 | 11.2538 |  |  |  | F | 1500 | 0 | 135 | 115 | AF | AJ+JD+DE+EF | 40.6105 | 74.3895 | 32.2451
Loop | DE | 8 | 130 | 400 | 717.8291 | 3.9556 | 0.010195 | 0.0025766 | 9.8891 |  |  |  | G | 750 | 0 | 80 | 170
JDEKI | EK | 8 | 130 | 750 | -252.6129 | -1.0743 | 0.0078675 | 0.0025766 | -1.4324 |  |  |  | H | 0 | 0 | 140 | 110
| KI | 8 | 130 | 750 | -703.3546 | -7.1425 | 0.018787 | 0.0025766 | -9.5234 |  |  |  | I | 0 | 800 | 80 | 170
| IJ | 8 | 130 | 400 | -1343.8896 | -12.6197 | 0.017372 | 0.0025766 | -31.5494 |  |  |  | J | 0 | 1200 | 120 | 130
[5 empty] | Sum | -0.00024424 | 0.09479 | 0 |  |  |  |  | K | 750 | 800 | 145 | 105
| IK | 8 | 130 | 750 | 703.3546 | 7.1425 | 0.018787 | 0.003718 | 9.5234
Loop | KG | 8 | 130 | 800 | 398.7886 | 2.6667 | 0.012371 | 0.003718 | 3.3334 |  |  |  | from Table 2 |  |  |  |  | Column with the elevation difference
IKGH | GH | 8 | 130 | 750 | -536.6288 | -4.3299 | 0.014927 | 0.003718 | -5.7732 | [8 empty] | referred to the elevation of the junction A
| HI | 8 | 130 | 800 | -588.582 | -5.4796 | 0.017223 | 0.003718 | -6.8495
[5 empty] | Sum | -0.00023538 | 0.063308 | 0
| KE | 8 | 130 | 750 | 252.6129 | 1.0743 | 0.0078675 | 0.0026484 | 1.4324
Loop | EF | 8 | 130 | 800 | 918.4889 | 12.4823 | 0.025142 | 0.0026484 | 15.6029
KEFG | FG | 8 | 130 | 750 | -883.4643 | -10.89 | 0.022804 | 0.0026484 | -14.52
| GK | 8 | 130 | 800 | -398.7886 | -2.6667 | 0.012371 | 0.0026484 | -3.3334
[5 empty] | Sum | -0.00018058 | 0.068184 | 0
8
Pipe velocities
[19 empty] | 1 gal = | 0.13368 | ft3
Table 7 | [18 empty] | 1gpm = | 0.13368 | ft/min
Data from Table 3 and Table 5 | [18 empty] | 1gpm = | 0.002228 | ft/s
Pipe Nº | Di | C | L | A | Q | Q | v
| in | - | ft | ft² | gpm | ft3/s | fps
A-J | 8 | 130 | 100 | 0.34907 | 2113.6719 | 4.7093 | 13.4911
J-D | 8 | 130 | 1500 | 0.34907 | 769.7822 | 1.7151 | 4.9134
D-E | 8 | 130 | 400 | 0.34907 | 717.8291 | 1.5993 | 4.5818
E-F | 8 | 130 | 800 | 0.34907 | 918.4889 | 2.0464 | 5.8625
F-G | 8 | 130 | 750 | 0.34907 | -883.4643 | -1.9684 | -5.639
G-H | 8 | 130 | 750 | 0.34907 | -536.6288 | -1.1956 | -3.4252
H-I | 8 | 130 | 800 | 0.34907 | -588.582 | -1.3114 | -3.7568
I-J | 8 | 130 | 400 | 0.34907 | -1343.8896 | -2.9942 | -8.5778
K-I | 8 | 130 | 750 | 0.34907 | 703.3546 | 1.5671 | 4.4894
E-K | 8 | 130 | 750 | 0.34907 | 252.6129 | 0.56283 | 1.6124
G-K | 8 | 130 | 800 | 0.34907 | 398.7886 | 0.88851 | 2.5454
9
| From Tables 5, 6 and 7 | [13 empty] | Flow rates solution
| Pipe Nº | Di | C | L | A | Q | Q | v | hf
|  | in | - | ft | ft² | gpm | ft3/s | fps | ft/kft |  |  |  | Source A |  |  |  | 769.7822
| A-J | 8 | 130 | 100 | 0.34907 | 2113.6719 | 4.7093 | 13.4911 | 73.6096 |  |  |  | 2113.6719 | J | 51.9531 |  |  |  |  | 51.9531 | D
| J-D | 8 | 130 | 1500 | 0.34907 | 769.7822 | 1.7151 | 4.9134 | 11.2538
| D-E | 8 | 130 | 400 | 0.34907 | 717.8291 | 1.5993 | 4.5818 | 9.8891 |  |  |  |  | 1343.8896
| E-F | 8 | 130 | 800 | 0.34907 | 918.4889 | 2.0464 | 5.8625 | 15.6029 | [11 empty] | 717.8291
| G-F | 8 | 130 | 750 | 0.34907 | 883.4643 | -1.9684 | -5.639 | -14.52
| H-G | 8 | 130 | 750 | 0.34907 | 536.6288 | -1.1956 | -3.4252 | -5.7732 |  |  | 1291.9365 |  | I |  | 703.3546 | K |  | 252.6129 |  | E
| I-H | 8 | 130 | 800 | 0.34907 | 588.582 | -1.3114 | -3.7568 | -6.8495 | [5 empty] | 51.9531 |  |  | 51.9531 |  | 51.9531
| J-I | 8 | 130 | 400 | 0.34907 | 1343.8896 | -2.9942 | -8.5778 | -31.5494
| I-K | 8 | 130 | 750 | 0.34907 | 703.3546 | 1.5671 | 4.4894 | -9.5234 |  |  |  |  | 588.582 |  |  |  | 398.7886
| K-E | 8 | 130 | 750 | 0.34907 | 252.6129 | 0.56283 | 1.6124 | -1.4324 | [11 empty] | 918.4889
| K-G | 8 | 130 | 800 | 0.34907 | 398.7886 | 0.88851 | 2.5454 | -3.3334
[13 empty] | Source C | H | 51.9531 |  | G | 51.9531 |  | 1801.9531 | F
| Consumptions in nodes | [14 empty] | 536.6288 |  |  | 883.4643
(from Table 1)
| Qj = | Di: DpJ =; C: 51.9531; L: gpm
| Qd = | Di: DpJ =; C: 51.9531; L: gpm
| Qi = | Di: DpJ =; C: 51.9531; L: gpm
| Qk = | Di: DpJ =; C: 51.9531; L: gpm
| Qe = | Di: DpJ =; C: 51.9531; L: gpm
| Qh = | Di: DpJ =; C: 51.9531; L: gpm
| Qg = | Di: DpJ =; C: 51.9531; L: gpm
| Qf = | Di: DPj + FF; C: 1801.9531; L: gpm

## Ref
[3] | Hardy Cross Part 1
by Kenneth Lamb
https://www.youtube.com/watch?v=pjUxSOCRVoo
[4] | Hardy Cross Part 2
by Kenneth Lamb
https://www.youtube.com/watch?v=t35MO1iMp4w
[5] | Hardy Cross Part 3
by Kenneth Lamb
https://www.youtube.com/watch?v=Tg4U3PdzzoY