## Hardy Cross_SI
1
Network analysis using the Hardy Cross method [3], [4] and [5]
The water system shown in Figure 1 has the folowing data:
| Table 1 | [5 empty] | Table 2 | [5 empty] | Table 3
|  | Junctions coordinates (m) |  |  |  |  | Total number of houses in the system
| Node | x-coord | y-coord | z-coord |  |  | (named as number of units Nu) | [5 empty] | Pipe diameters, Hazen-Williams constant
Reservoir | A | -30.48 | 365.76 | 76.2 |  |  | Nu = | 300 | units |  |  |  | and lengths
1 | D | 457.2 | 365.76 | 30.48
2 | E | 457.2 | 243.84 | 24.384 |  |  | Average day unit demnad | [5 empty] | Pipe ID | D (m) | C | L (m)
3 | F | 457.2 | 0 | 41.148 |  |  | q = | 4315.3674 | lt/(day*unit) |  |  |  | JD | 0.2032 | 130 | 457.2
4 | G | 228.6 | 0 | 24.384 | [8 empty] | DE | 0.2032 | 130 | 121.92
5 | H | 0 | 0 | 42.672 |  |  | Nº of junctions | [5 empty] | EK | 0.2032 | 130 | 228.6
6 | I | 0 | 243.84 | 24.384 |  |  | Nj = | 8 | - |  |  |  | KI | 0.2032 | 130 | 228.6
7 | J | 0 | 365.76 | 36.576 | [8 empty] | IJ | 0.2032 | 130 | 121.92
8 | K | 228.6 | 243.84 | 44.196 |  |  | Maximum Day Factor
[7 empty] | MDF = | 1.75 | - |  |  |  | IK | 0.2032 | 130 | 228.6
[13 empty] | KG | 0.2032 | 130 | 243.84
[7 empty] | Fire flow | [5 empty] | GH | 0.2032 | 130 | 228.6
[7 empty] | FF = | 6624.4675 | lt/min |  |  |  | HI | 0.2032 | 130 | 243.84
[13 empty] | KE | 0.2032 | 130 | 228.6
[13 empty] | EF | 0.2032 | 130 | 243.84
[13 empty] | FG | 0.2032 | 130 | 228.6
[13 empty] | GK | 0.2032 | 130 | 243.84
To see the original document, see | [12 empty] | AJ | 0.2032 | 130 | 30.48
www.piping-tools.net
Pipes. Network analysis using the Hardy Cross method _Imperial units
or the youtube presentations [3], [4] and [5] | [12 empty] | Note. Length could be obtained from Table 1
2
1.- Assign flow directions in the loops
2.- Water demand in each junction
A clockweise direction is assigned as positive | [16 empty] | 4.- Assing flow values to the map
[6 empty] | In the example the demands are defined |  |  |  |  | 3.- Assign the fire flow to junction F | [5 empty] | With data from Table 4
[6 empty] | as follows |  |  |  |  | Fire Flow
[11 empty] | FF = | 6624.4675 | Lt/min |  |  | Source A
[6 empty] | Average day demand in the system: AD | [10 empty] | J | 196.6639 |  |  |  |  | 196.6639 | D
[6 empty] | AD = | Nu* q
[6 empty] | NU = | 300 | units |  |  | Consumption at the nodes
[6 empty] | q = | 4315.3674 | lt/(day*unit) |  |  | Table 4
[6 empty] | AD = | 1294610.22 | lt/(day*system) |  |  | Consumptions in nodes
[11 empty] | Qj = | DpJ = | 196.6639 | lt/min |  |  | I |  |  | K |  |  |  | E
[6 empty] | Average minute demand: AmD |  |  |  |  | Qd = | DpJ = | 196.6639 | lt/min |  |  |  | 196.6639 |  |  | 196.6639 |  | 196.6639
[6 empty] | AmD = | AD / (24*60) |  |  |  | Qi = | DpJ = | 196.6639 | lt/min
[6 empty] | AmD = | 899.0349 | lt/(min*system) |  |  | Qk = | DpJ = | 196.6639 | lt/min
[11 empty] | Qe = | DpJ = | 196.6639 | lt/min
[6 empty] | Maximum day demand : MDD |  |  |  |  | Qh = | DpJ = | 196.6639 | lt/min
[6 empty] | MDD = | AmD * MDF |  |  |  | Qg = | DpJ = | 196.6639 | lt/min
[6 empty] | AmD = | 899.0349 | lLt/(h*system) |  |  | Qf = | DPj + FF | 6821.1314 | lt/min |  | Source C | H | 196.6639 |  | G | 196.6639 |  | 6821.1314 | F
[6 empty] | MDF = | 1.75 | -
[6 empty] | MDD = | 1573.311 | lt/(min*system) |  |  | System demand | [8 empty] | Figure 3
[11 empty] | SD = | MDD + FF
[6 empty] | Assuming that all junction demans are |  |  |  |  | MDD = | 1573.311 | lt/(min*system)
[6 empty] | the same |  |  |  |  | FF = | 6624.4675 | lt/min
[6 empty] | Demand per Junction: DpJ |  |  |  |  | SD = | 8197.7785 | lt/min
[6 empty] | DpJ = | MDD / Nj
[6 empty] | MDD = | 1573.311 | lt/(min*system)
[6 empty] | Nj = | 8
[6 empty] | DpJ = | 196.6639 | lt/(min*junction)
3
5. Asign flow rates and flow directions to the pipes | [17 empty] | Q [lt/min]
[12 empty] | Source A | 8001.1147 |  |  | 393.3278
Table 5 | [12 empty] | J | 196.6639 |  |  |  |  | 196.6639 | D
Balance in node K
Assigned flows and calculated | [6 empty] | Qik = | Qk + Qkg + Qke |  |  |  |  | 7607.7869
values | [6 empty] | Qk = | 196.6639 | [11 empty] | 196.6639
Let |  |  |  | Balance in node E |  |  | Qkg = | 50
Qgf = | QF/2 |  |  | Qke + Qde = Qe + Qef |  |  | Qke = | 3410.5657 |  |  |  |  | I |  | 3657.2296 | K |  | 3410.5657 |  | E
Qf = | 6821.1314 | lt/min |  | Qde = | Qe + Qef - Qke |  | Qik = | 3657.2296 | lt/min |  |  |  |  | 196.6639 |  |  | 196.6639 |  | 196.6639
Qgf = | 3410.5657 | lt/min |  | Qe = | 196.6639
|  |  |  | Qef = | 3410.5657 |  | Balance in node H | [5 empty] | 3753.8934 |  |  |  | 50
Balance in node F |  |  |  | Qke = | 3410.5657 |  | Qih = | Qh + Qhg | [11 empty] | 3410.5657
Qef = | Qf - Qgf |  |  | Qde = | 196.6639 | lt/min | Qh = | 196.6639
Qf = | 6821.1314 | [5 empty] | Qhg = | 3557.2296
Qgf = | 3410.5657 |  |  | Balance in nodeD |  |  | Qih = | 3753.8934 | lt/min |  |  | Source C | H | 196.6639 |  | G | 196.6639 |  | 6821.1314 | F
Qef = | 3410.5657 | lt/min |  | Qjd = | Qd+Qde | [9 empty] | 3557.2296 |  |  | 3410.5657
|  |  |  | Qd = | 196.6639 |  | Balance in node I
Let |  |  |  | Qde = | 196.6639 |  | Qji = | Qi + Qih + Qik | [6 empty] | Figure 4
Qke = | Qef |  |  | Qjd = | 393.3278 | lt/min | Qi = | 196.6639
Qke = | 3410.5657 | lt/min |  |  |  |  | Qih = | 3753.8934
|  |  |  | Balancein node G |  |  | Qik = | 3657.2296
Let |  |  |  | QHg + Qkg = Qg + Qgf |  |  | Qji = | 7607.7869 | lt/min
Qkg = | 50 | lt/min |  | QHg = | Qg + Qgf - Qkg
|  |  |  | Qg = | 196.6639 |  | Balance in node J
FF = | 6624.4675 | lt/min |  | Qgf = | 3410.5657 |  | QAJ = | Qji + QJD
|  |  |  | Qkg = | 50 |  | QJI = | 7607.7869
|  |  |  | QHg = | 3557.2296 | lt/min | Q JD = | 393.3278
[7 empty] | QAJ = | 8001.1147 | lt/min
[7 empty] | QAJ = | 0.13335 | m3/s
[20 empty] | Q [m3/s] |  |  |  |  | 4
6.- Tabulate flows obtained in Table 5 |  |  |  |  | 7.- Assign signs of flows, according Figure 4
(change the flow units to m3/s) | [14 empty] | Source A | 0 |  |  | 0.0065555
[6 empty] | Input information for the pipe running from thr reservoir to the first | [9 empty] | J | 196.6639 |  |  |  |  | 196.6639 | D
system junction
[6 empty] | Pipe ID | D (m) | C | L (m) | r | Q (m3/s) | h (m) |  |  |  | -0.1268
[6 empty] | A-J | 0.2032 | 130 | 30.48 |  | 0.13335 | [11 empty] | 0.0032777
[10 empty] | (Eq.1) | Note 1
Table 6 |  |  |  |  | Table 7 | [10 empty] | I |  | -0.060954 | K |  | -0.056843 |  | E
[17 empty] | 0 |  |  | 0 |  | 0
| Pipe ID | Q (m3/s) |  |  |  | Pipe ID | D (m) | C | L (m) | r | Q (m3/s) | h (m)
|  | Note 1 | [8 empty] | Note 1 |  |  |  |  | 3753.8934 |  |  |  | 50
| JD | 0.0065555 |  |  |  | JD | 0.2032 | 130 | 457.2 |  | 0.0065555 | [11 empty] | 3410.5657
Loop | DE | 0.0032777 |  |  | Loop | DE | 0.2032 | 130 | 121.92 |  | 0.0032777
JDEKI | EK | 0.056843 |  |  | JDEKI | EK | 0.2032 | 130 | 228.6 |  | -0.056843
| KI | 0.060954 |  |  |  | KI | 0.2032 | 130 | 228.6 |  | -0.060954 |  |  |  | Source C | H | 0 |  | G | 0 |  | 0 | F
| IJ | 0.1268 |  |  |  | IJ | 0.2032 | 130 | 121.92 |  | -0.1268 | [6 empty] | 3557.2296 |  |  | 3410.5657
| IK | 0.060954 |  |  |  | IK | 0.2032 | 130 | 228.6 |  | 0.060954 | [6 empty] | Figure 4 (repeated)
Loop | KG | 0.00083333 |  |  | Loop | KG | 0.2032 | 130 | 243.84 |  | 0.00083333
IKGH | GH | 0.059287 |  |  | IKGH | GH | 0.2032 | 130 | 228.6 |  | -0.059287
| HI | 0.062565 |  |  |  | HI | 0.2032 | 130 | 243.84 |  | -0.062565
| KE | 0.056843 |  |  |  | KE | 0.2032 | 130 | 228.6 |  | 0.056843
Loop | EF | 0.056843 |  |  | Loop | EF | 0.2032 | 130 | 243.84 |  | 0.056843
KEFG | FG | 0.056843 |  |  | KEFG | FG | 0.2032 | 130 | 228.6 |  | -0.056843
| GK | 0.00083333 |  |  |  | GK | 0.2032 | 130 | 243.84 |  | -0.00083333
| AJ | 0.13335 |  |  |  | AJ | 0.2032 | 130 | 30.48 |  | 0.13335
Note 1. | From Table 5, or Figure 4
5
8. Hazen Wiliams equations (metric system) [7]
| Pipe length |  | L | m
| Flow rate |  | Q | m3/s
| Hazen Williams | [15 empty] | hf =10.626 * L * Q^1.85 / (C^0.85 * d^4.867 ) |  |  |  | (Eq. d)
| roughness coefficient |  | C | -
| Pipe diameter |  | d | m
| Friction pressure loss |  | hf | m
| Hydraulic radius |  | Rh | m
| Mean velocity |  | v | m/s
| Friction slope |  | S | m/m
[17 empty] | r = | 10.626 * L / ( C^1.85 * d^4.867 ) |  |  | (Eq. e)
Hazen Williams empirical equation for friction head loss
The Hazen Williams equation was developed for water at
temperatures normally experienced in potable water
systems, for pipe diameters d >= 50 mm and within a
moderate range of water velocity v <= 3 m/s.
[17 empty] | hf = | r * Q^1.85 |  | (Eq. f)
6
9.- Iterations. Table 8
[9 empty] | Modification of (Eq.f) to allow for a | [8 empty] | n = | 1.85 |  | Shared pipes
[9 empty] | a copy-paste method for the next | [11 empty] | For example, shared pipes shown in green cells
[9 empty] | iterations. | [11 empty] | In this case, the adjusted flow will be
r = | 10.626 * L / ( C^1.85 * d^4.867 ) |  |  |  | hf = | r * Q^1.85 |  |  | IF(Q<0,-h*ABS(Q)^1.85,$r*ABS(Q)^1.85) | [11 empty] | Qajd(EK) = | Qini(EK) + DQ(EK) - DQ(KE)
Input information for the pipe running from thr reservoir to the first system junction
| Pipe ID | D (m) | C | L (m) | r | Q (m3/s) | h (m) | R
[5 empty] | (Eq.e) |  | (Eq.f) | (Eq.3)
| A-J | 0.2032 | 130 | 30.48 | 92.8806 | 0.13335 | 2.2345 | 30.9989
| 1 | iteration | [7 empty] | 2 | iteration |  |  | 3 | iteration |  |  | 4 | iteration |  |  | 5 | iteration |  |  | 6 | iteration |  |  | 7 | iteration |  |  | 8 | iteration |  |  | 9 | iteration |  |  | 10 | iteration |  |  | 11 | iteration |  |  | 12 | iteration
| Pipe ID | D (m) | C | L (m) | r | Q (m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | Qadj(m3/s) | h (m) | R | DQ (m3/s)
[5 empty] | (Eq. e) | (from Table 7) | (Eq.f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4)
| JD | 0.2032 | 130 | 457.2 | 1399.8851 | 0.0065555 | 0.12788 | 36.0892 | 0.039278 | 0.045834 | 4.6697 | 188.4834 | -0.00069574 | 0.045138 | 4.5394 | 186.0486 | 0.0026017 | 0.04774 | 5.0353 | 195.1253 | 0.00045237 | 0.048192 | 5.1239 | 196.6958 | 0.00025721 | 0.048449 | 5.1746 | 197.5878 | 7.0341e-05 | 0.04852 | 5.1885 | 197.8316 | 3.0677e-05 | 0.048551 | 5.1946 | 197.9379 | 9.6016e-06 | 0.04856 | 5.1965 | 197.9711 | 3.8134e-06 | 0.048564 | 5.1972 | 197.9844 | 1.2712e-06 | 0.048565 | 5.1975 | 197.9888 | 4.818e-07 | 0.048566 | 5.1976 | 197.9904 | 1.6609e-07
Loop | DE | 0.2032 | 130 | 121.92 | 373.3027 | 0.0032777 | 0.0094596 | 5.3391 | 0.039278 | 0.042556 | 1.0855 | 47.1901 | -0.00069574 | 0.04186 | 1.0529 | 46.5335 | 0.0026017 | 0.044462 | 1.1772 | 48.9807 | 0.00045237 | 0.044915 | 1.1994 | 49.404 | 0.00025721 | 0.045172 | 1.2122 | 49.6444 | 7.0341e-05 | 0.045242 | 1.2157 | 49.7101 | 3.0677e-05 | 0.045273 | 1.2172 | 49.7387 | 9.6016e-06 | 0.045282 | 1.2177 | 49.7477 | 3.8134e-06 | 0.045286 | 1.2179 | 49.7512 | 1.2712e-06 | 0.045287 | 1.2179 | 49.7524 | 4.818e-07 | 0.045288 | 1.2179 | 49.7529 | 1.6609e-07
JDEKI | EK | 0.2032 | 130 | 228.6 | 699.9426 | -0.056843 | -3.4771 | 113.1639 | 0.039278 | -0.006983 | -0.07187 | 19.0402 | -0.00069574 | -0.016961 | -0.37114 | 40.4819 | 0.0026017 | -0.01578 | -0.32478 | 38.0746 | 0.00045237 | -0.015949 | -0.33123 | 38.4205 | 0.00025721 | -0.015931 | -0.33055 | 38.3842 | 7.0341e-05 | -0.015937 | -0.33077 | 38.3958 | 3.0677e-05 | -0.015937 | -0.33076 | 38.3952 | 9.6016e-06 | -0.015937 | -0.33077 | 38.3961 | 3.8134e-06 | -0.015937 | -0.33077 | 38.3961 | 1.2712e-06 | -0.015937 | -0.33078 | 38.3962 | 4.818e-07 | -0.015937 | -0.33078 | 38.3962 | 1.6609e-07
| KI | 0.2032 | 130 | 228.6 | 699.9426 | -0.060954 | -3.9565 | 120.0839 | 0.039278 | -0.033056 | -1.2755 | 71.3826 | -0.00069574 | -0.04458 | -2.218 | 92.0454 | 0.0026017 | -0.043714 | -2.139 | 90.5238 | 0.00045237 | -0.044311 | -2.1934 | 91.5736 | 0.00025721 | -0.04431 | -2.1932 | 91.5711 | 7.0341e-05 | -0.044363 | -2.1981 | 91.6638 | 3.0677e-05 | -0.044368 | -2.1985 | 91.6727 | 9.6016e-06 | -0.044373 | -2.199 | 91.6822 | 3.8134e-06 | -0.044374 | -2.1991 | 91.684 | 1.2712e-06 | -0.044375 | -2.1992 | 91.685 | 4.818e-07 | -0.044375 | -2.1992 | 91.6853 | 1.6609e-07
| IJ | 0.2032 | 130 | 121.92 | 373.3027 | -0.1268 | -8.1811 | 119.3641 | 0.039278 | -0.087518 | -4.1204 | 87.0995 | -0.00069574 | -0.088214 | -4.1812 | 87.6877 | 0.0026017 | -0.085612 | -3.9559 | 85.4845 | 0.00045237 | -0.08516 | -3.9174 | 85.1004 | 0.00025721 | -0.084902 | -3.8955 | 84.8819 | 7.0341e-05 | -0.084832 | -3.8895 | 84.8221 | 3.0677e-05 | -0.084801 | -3.8869 | 84.796 | 9.6016e-06 | -0.084792 | -3.8861 | 84.7878 | 3.8134e-06 | -0.084788 | -3.8858 | 84.7846 | 1.2712e-06 | -0.084787 | -3.8857 | 84.7835 | 4.818e-07 | -0.084786 | -3.8856 | 84.7831 | 1.6609e-07
[6 empty] | Sum | -15.4773 | 394.0403 |  | Sum | 0.28748 | 413.1959 |  | Sum | -1.1781 | 452.7972 |  | Sum | -0.20727 | 458.189 |  | Sum | -0.11862 | 461.1943 |  | Sum | -0.032503 | 462.0692 |  | Sum | -0.014186 | 462.4232 |  | Sum | -0.0044411 | 462.5405 |  | Sum | -0.001764 | 462.585 |  | Sum | -0.00058806 | 462.6003 |  | Sum | -0.00022289 | 462.606 |  | Sum | -7.6835e-05 | 462.608
| IK | 0.2032 | 130 | 228.6 | 699.9426 | 0.060954 | 3.9565 | 120.0839 | 0.01138 | 0.033056 | 1.2755 | 71.3826 | 0.010828 | 0.04458 | 2.218 | 92.0454 | 0.0017361 | 0.043714 | 2.139 | 90.5238 | 0.0010494 | 0.044311 | 2.1934 | 91.5736 | 0.00025575 | 0.04431 | 2.1932 | 91.5711 | 0.00012312 | 0.044363 | 2.1981 | 91.6638 | 3.5727e-05 | 0.044368 | 2.1985 | 91.6727 | 1.5047e-05 | 0.044373 | 2.199 | 91.6822 | 4.8073e-06 | 0.044374 | 2.1991 | 91.684 | 1.8815e-06 | 0.044375 | 2.1992 | 91.685 | 6.3365e-07 | 0.044375 | 2.1992 | 91.6853 | 2.3835e-07
Loop | KG | 0.2032 | 130 | 243.84 | 746.6054 | 0.00083333 | 0.0015018 | 3.3339 | 0.01138 | 0.022795 | 0.68405 | 55.5167 | 0.010828 | 0.024341 | 0.77238 | 58.7025 | 0.0017361 | 0.024656 | 0.79095 | 59.3467 | 0.0010494 | 0.025084 | 0.81655 | 60.2217 | 0.00025575 | 0.0251 | 0.81753 | 60.255 | 0.00012312 | 0.025148 | 0.82037 | 60.3511 | 3.5727e-05 | 0.025153 | 0.82069 | 60.3619 | 1.5047e-05 | 0.025158 | 0.82099 | 60.3722 | 4.8073e-06 | 0.025159 | 0.82105 | 60.3742 | 1.8815e-06 | 0.025159 | 0.82109 | 60.3753 | 6.3365e-07 | 0.02516 | 0.8211 | 60.3756 | 2.3835e-07
IKGH | GH | 0.2032 | 130 | 228.6 | 699.9426 | -0.059287 | -3.7587 | 117.2872 | 0.01138 | -0.047907 | -2.534 | 97.8526 | 0.010828 | -0.037078 | -1.5774 | 78.7022 | 0.0017361 | -0.035342 | -1.4435 | 75.5589 | 0.0010494 | -0.034293 | -1.3652 | 73.6476 | 0.00025575 | -0.034037 | -1.3464 | 73.1805 | 0.00012312 | -0.033914 | -1.3374 | 72.9554 | 3.5727e-05 | -0.033878 | -1.3348 | 72.8901 | 1.5047e-05 | -0.033863 | -1.3337 | 72.8625 | 4.8073e-06 | -0.033859 | -1.3334 | 72.8538 | 1.8815e-06 | -0.033857 | -1.3332 | 72.8503 | 6.3365e-07 | -0.033856 | -1.3332 | 72.8492 | 2.3835e-07
| HI | 0.2032 | 130 | 243.84 | 746.6054 | -0.062565 | -4.429 | 130.9616 | 0.01138 | -0.051185 | -3.0549 | 110.4159 | 0.010828 | -0.040356 | -1.968 | 90.2165 | 0.0017361 | -0.03862 | -1.8142 | 86.9069 | 0.0010494 | -0.037571 | -1.7241 | 84.8955 | 0.00025575 | -0.037315 | -1.7025 | 84.4041 | 0.00012312 | -0.037192 | -1.6921 | 84.1673 | 3.5727e-05 | -0.037156 | -1.6891 | 84.0986 | 1.5047e-05 | -0.037141 | -1.6878 | 84.0696 | 4.8073e-06 | -0.037136 | -1.6874 | 84.0604 | 1.8815e-06 | -0.037134 | -1.6872 | 84.0567 | 6.3365e-07 | -0.037134 | -1.6872 | 84.0555 | 2.3835e-07
[6 empty] | Sum | -4.2297 | 371.6667 | 0.01138 | Sum | -3.6294 | 335.1679 |  | Sum | -0.55496 | 319.6667 |  | Sum | -0.32776 | 312.3363 |  | Sum | -0.07937 | 310.3384 |  | Sum | -0.038096 | 309.4106 |  | Sum | -0.011045 | 309.1376 |  | Sum | -0.00465 | 309.0232 |  | Sum | -0.0014854 | 308.9865 |  | Sum | -0.00058134 | 308.9722 |  | Sum | -0.00019578 | 308.9674 |  | Sum | -7.3641e-05 | 308.9656
| KE | 0.2032 | 130 | 228.6 | 699.9426 | 0.056843 | 3.4771 | 113.1639 | -0.010581 | 0.006983 | 0.07187 | 19.0402 | 0.0092819 | 0.016961 | 0.37114 | 40.4819 | 0.0014215 | 0.01578 | 0.32478 | 38.0746 | 0.00062116 | 0.015949 | 0.33123 | 38.4205 | 0.00023944 | 0.015931 | 0.33055 | 38.3842 | 7.6006e-05 | 0.015937 | 0.33077 | 38.3958 | 3.0417e-05 | 0.015937 | 0.33076 | 38.3952 | 1.002e-05 | 0.015937 | 0.33077 | 38.3961 | 3.8375e-06 | 0.015937 | 0.33077 | 38.3961 | 1.3122e-06 | 0.015937 | 0.33078 | 38.3962 | 4.8805e-07 | 0.015937 | 0.33078 | 38.3962 | 1.7056e-07
Loop | EF | 0.2032 | 130 | 243.84 | 746.6054 | 0.056843 | 3.7089 | 120.7082 | -0.010581 | 0.046262 | 2.5337 | 101.321 | 0.0092819 | 0.055543 | 3.5535 | 118.3588 | 0.0014215 | 0.056965 | 3.7236 | 120.9287 | 0.00062116 | 0.057586 | 3.7991 | 122.0486 | 0.00023944 | 0.057826 | 3.8284 | 122.4798 | 7.6006e-05 | 0.057902 | 3.8377 | 122.6166 | 3.0417e-05 | 0.057932 | 3.8414 | 122.6714 | 1.002e-05 | 0.057942 | 3.8426 | 122.6894 | 3.8375e-06 | 0.057946 | 3.8431 | 122.6963 | 1.3122e-06 | 0.057947 | 3.8433 | 122.6987 | 4.8805e-07 | 0.057948 | 3.8433 | 122.6996 | 1.7056e-07
KEFG | FG | 0.2032 | 130 | 228.6 | 699.9426 | -0.056843 | -3.4771 | 113.1639 | -0.010581 | -0.067424 | -4.7684 | 130.8358 | 0.0092819 | -0.058142 | -3.6255 | 115.3589 | 0.0014215 | -0.056721 | -3.4632 | 112.9572 | 0.00062116 | -0.056099 | -3.3934 | 111.9048 | 0.00023944 | -0.05586 | -3.3667 | 111.4987 | 7.6006e-05 | -0.055784 | -3.3582 | 111.3698 | 3.0417e-05 | -0.055754 | -3.3548 | 111.3181 | 1.002e-05 | -0.055744 | -3.3537 | 111.3011 | 3.8375e-06 | -0.05574 | -3.3533 | 111.2946 | 1.3122e-06 | -0.055738 | -3.3531 | 111.2924 | 4.8805e-07 | -0.055738 | -3.3531 | 111.2916 | 1.7056e-07
| GK | 0.2032 | 130 | 243.84 | 746.6054 | -0.00083333 | -0.0015018 | 3.3339 | -0.010581 | -0.022795 | -0.68405 | 55.5167 | 0.0092819 | -0.024341 | -0.77238 | 58.7025 | 0.0014215 | -0.024656 | -0.79095 | 59.3467 | 0.00062116 | -0.025084 | -0.81655 | 60.2217 | 0.00023944 | -0.0251 | -0.81753 | 60.255 | 7.6006e-05 | -0.025148 | -0.82037 | 60.3511 | 3.0417e-05 | -0.025153 | -0.82069 | 60.3619 | 1.002e-05 | -0.025158 | -0.82099 | 60.3722 | 3.8375e-06 | -0.025159 | -0.82105 | 60.3742 | 1.3122e-06 | -0.025159 | -0.82109 | 60.3753 | 4.8805e-07 | -0.02516 | -0.8211 | 60.3756 | 1.7056e-07
[6 empty] | Sum | 3.7074 | 350.37 |  | Sum | -2.8469 | 306.7138 |  | Sum | -0.47322 | 332.9022 |  | Sum | -0.2058 | 331.3072 |  | Sum | -0.079638 | 332.5957 |  | Sum | -0.025281 | 332.6177 |  | Sum | -0.010121 | 332.7333 |  | Sum | -0.003334 | 332.7467 |  | Sum | -0.001277 | 332.7588 |  | Sum | -0.00043664 | 332.7612 |  | Sum | -0.0001624 | 332.7626 |  | Sum | -5.6756e-05 | 332.763
7
Pressure loss per 1000 m | [11 empty] | Residual pressure at the junctions
Table 9 | [11 empty] | Table 10
Pipe ID |  | D (m) | C | L (m) | r | Q (m3/s) | h (m) |  | hfk | [8 empty] | Pressure losses between node A and
|  |  |  | (Eq.1) |  | (Eq.2) | (Eq.f) |  | m/(1000m) |  |  |  |  | Coordinates (ft) |  |  | DEL | the selected node |  |  | Residual pressure
A-J | A-J | 0.2032 | 130 | 30.48 | 92.8806 | 0.13335 | 2.2345 |  | 73.3092 |  |  |  | Node i | x-coord | y-coord | z-coord | ELA - ELi |  |  | DP | Presidual = DEL - DP
[14 empty] | ft | ft | ft | ft |  |  | ft | ft | psi
| 1 | iteration |  |  | 12 | iteration | [5 empty] | Reservoir | A | -100 | 1200 | 76.2 |  | AJ |  | 2.2345
| Pipe ID | D (mn) | C | L (m) | Qadj(m3/s) | h (m) | R | DQ (m3/s) | hfk |  |  |  | D | 1500 | 1200 | 30.48 | 45.72 | AD | AJ + JD | 7.4321 | 38.2879 | 16.5964
[5 empty] | (Eq.5) | (Eq. f) | (Eq.3) | (Eq. 4) | m/km |  |  |  | E | 1500 | 800 | 24.384 | 51.816
| JD | 0.2032 | 130 | 457.2 | 0.048566 | 5.1976 | 197.9904 | 1.6609e-07 | 11.3683 |  |  |  | F | 1500 | 0 | 41.148 | 35.052 | AF | AJ+JD+DE+EF | 12.4933 | 22.5587 | 9.7784
Loop | DE | 0.2032 | 130 | 121.92 | 0.045288 | 1.2179 | 49.7529 | 1.6609e-07 | 9.9897 |  |  |  | G | 750 | 0 | 24.384 | 51.816
JDEKI | EK | 0.2032 | 130 | 228.6 | -0.015937 | -0.33078 | 38.3962 | 1.6609e-07 | -1.447 |  |  |  | H | 0 | 0 | 42.672 | 33.528
| KI | 0.2032 | 130 | 228.6 | -0.044375 | -2.1992 | 91.6853 | 1.6609e-07 | -9.6203 |  |  |  | I | 0 | 800 | 24.384 | 51.816
| IJ | 0.2032 | 130 | 121.92 | -0.084786 | -3.8856 | 84.7831 | 1.6609e-07 | -31.8704 |  |  |  | J | 0 | 1200 | 36.576 | 39.624
[5 empty] | Sum | -7.6835e-05 | 462.608 | 0 |  |  |  |  | K | 750 | 800 | 44.196 | 32.004
| IK | 0.2032 | 130 | 228.6 | 0.044375 | 2.1992 | 91.6853 | 2.3835e-07 | 9.6203
Loop | KG | 0.2032 | 130 | 243.84 | 0.02516 | 0.8211 | 60.3756 | 2.3835e-07 | 3.3674 |  |  |  | from Table 1 |  |  |  |  | Column with the elevation difference
IKGH | GH | 0.2032 | 130 | 228.6 | -0.033856 | -1.3332 | 72.8492 | 2.3835e-07 | -5.8319 | [8 empty] | referred to the elevation of the junction A
| HI | 0.2032 | 130 | 243.84 | -0.037134 | -1.6872 | 84.0555 | 2.3835e-07 | -6.9192
[5 empty] | Sum | -7.3641e-05 | 308.9656 | 0
| KE | 0.2032 | 130 | 228.6 | 0.015937 | 0.33078 | 38.3962 | 1.7056e-07 | 1.447
Loop | EF | 0.2032 | 130 | 243.84 | 0.057948 | 3.8433 | 122.6996 | 1.7056e-07 | 15.7617
KEFG | FG | 0.2032 | 130 | 228.6 | -0.055738 | -3.3531 | 111.2916 | 1.7056e-07 | -14.6678
| GK | 0.2032 | 130 | 243.84 | -0.02516 | -0.8211 | 60.3756 | 1.7056e-07 | -3.3674
[5 empty] | Sum | -5.6756e-05 | 332.763 | 0
8
Pipe velocities
Table 11
Data from Table 7 and Table 9
Pipe Nº | Di | C | L | A | Q | v
| m | - | m | m² | m3/s | m/s
A-J | 0.2032 | 130 | 30.48 | 0.032429 | 0.13335 | 4.1121
J-D | 0.2032 | 130 | 457.2 | 0.032429 | 0.048566 | 1.4976
D-E | 0.2032 | 130 | 121.92 | 0.032429 | 0.045288 | 1.3965
E-F | 0.2032 | 130 | 243.84 | 0.032429 | 0.057948 | 1.7869
F-G | 0.2032 | 130 | 228.6 | 0.032429 | -0.055738 | -1.7188
G-H | 0.2032 | 130 | 228.6 | 0.032429 | -0.033856 | -1.044
H-I | 0.2032 | 130 | 243.84 | 0.032429 | -0.037134 | -1.1451
I-J | 0.2032 | 130 | 121.92 | 0.032429 | -0.084786 | -2.6145
K-I | 0.2032 | 130 | 228.6 | 0.032429 | 0.044375 | 1.3684
E-K | 0.2032 | 130 | 228.6 | 0.032429 | 0.015937 | 0.49145
G-K | 0.2032 | 130 | 243.84 | 0.032429 | 0.02516 | 0.77583
9
Table 12
| From Tables 11 and 9 | [13 empty] | Flow rates solution Q (m3/s)
| Pipe Nº | Di | C | L | A | Q | v | hf
|  | m | - | m | m² | m3/s | m/s | m/km |  |  |  |  | Source A |  |  |  | 0.048566
| A-J | 0.2032 | 130 | 30.48 | 0.032429 | 0.13335 | 4.1121 | 73.3092 |  |  |  |  | 0.13335 | J | 196.6639 |  |  |  |  | 196.6639 | D
| J-D | 0.2032 | 130 | 457.2 | 0.032429 | 0.048566 | 1.4976 | 11.3683
| D-E | 0.2032 | 130 | 121.92 | 0.032429 | 0.045288 | 1.3965 | 9.9897 | [5 empty] | 0.084786
| E-F | 0.2032 | 130 | 243.84 | 0.032429 | 0.057948 | 1.7869 | 15.7617 | [12 empty] | 0.045288
| G-F | 0.2032 | 130 | 228.6 | 0.032429 | 0.055738 | -1.7188 | -14.6678
| H-G | 0.2032 | 130 | 228.6 | 0.032429 | 0.033856 | -1.044 | -5.8319 | [5 empty] | I |  | 0.044375 | K |  | 0.015937 |  | E
| I-H | 0.2032 | 130 | 243.84 | 0.032429 | 0.037134 | -1.1451 | -6.9192 | [6 empty] | 196.6639 |  |  | 196.6639 |  | 196.6639
| J-I | 0.2032 | 130 | 121.92 | 0.032429 | 0.084786 | -2.6145 | -31.8704
| I-K | 0.2032 | 130 | 228.6 | 0.032429 | 0.044375 | 1.3684 | -9.6203 | [5 empty] | 0.037134 |  |  |  | 0.02516
| K-E | 0.2032 | 130 | 228.6 | 0.032429 | 0.015937 | 0.49145 | -1.447 | [12 empty] | 0.057948
| K-G | 0.2032 | 130 | 243.84 | 0.032429 | 0.02516 | 0.77583 | -3.3674
[13 empty] | Source C | H | 196.6639 |  | G | 196.6639 |  | 6821.1314 | F
| Consumptions in nodes | [14 empty] | 0.033856 |  |  | 0.055738
(from Table 41)
| Qj = | DpJ = | 196.6639 | lt/min
| Qd = | DpJ = | 196.6639 | lt/min
| Qi = | DpJ = | 196.6639 | lt/min
| Qk = | DpJ = | 196.6639 | lt/min
| Qe = | DpJ = | 196.6639 | lt/min
| Qh = | DpJ = | 196.6639 | lt/min
| Qg = | DpJ = | 196.6639 | lt/min
| Qf = | DPj + FF | 6821.1314 | lt/min
System demand
| SD = | 8197.7785 | lt/min
10
Table 12 |  | Obtained results | [6 empty] | Results from [3], expressed in SI units | [8 empty] | Results from [3] in Imperial units
Pipe Nº | Di | C | L | A | Q | v | hf |  | Pipe Nº | Di | C | L | A | Q | v | hf |  | Pipe Nº | Di | C | L | A | Q | Q | v | hf
| m | - | m | m² | m3/s | m/s | m/km |  |  | m | - | m | m² | m3/s | m/s | m/km |  |  | in | - | ft | ft² | gpm | ft3/s | fps | ft/kft
A-J | 0.2032 | 130 | 30.48 | 0.032429 | 0.13335 | 4.1121 | 73.3092 |  | A-J | 0.2032 | 130 | 30.48 | 0.032429 | 0.13335 | 4.1121 | 73.6096 |  | A-J | 8 | 130 | 100 | 0.34907 | 2113.6719 | 4.7093 | 13.4911 | 73.6096
J-D | 0.2032 | 130 | 457.2 | 0.032429 | 0.048566 | 1.4976 | 11.3683 |  | J-D | 0.2032 | 130 | 457.2 | 0.032429 | 0.048566 | 1.4976 | 11.2538 |  | J-D | 8 | 130 | 1500 | 0.34907 | 769.7822 | 1.7151 | 4.9134 | 11.2538
D-E | 0.2032 | 130 | 121.92 | 0.032429 | 0.045288 | 1.3965 | 9.9897 |  | D-E | 0.2032 | 130 | 121.92 | 0.032429 | 0.045288 | 1.3965 | 9.8891 |  | D-E | 8 | 130 | 400 | 0.34907 | 717.8291 | 1.5993 | 4.5818 | 9.8891
E-F | 0.2032 | 130 | 243.84 | 0.032429 | 0.057948 | 1.7869 | 15.7617 |  | E-F | 0.2032 | 130 | 243.84 | 0.032429 | 0.057948 | 1.7869 | 15.6029 |  | E-F | 8 | 130 | 800 | 0.34907 | 918.4889 | 2.0464 | 5.8625 | 15.6029
G-F | 0.2032 | 130 | 228.6 | 0.032429 | 0.055738 | -1.7188 | -14.6678 |  | G-F | 0.2032 | 130 | 228.6 | 0.032429 | 0.055738 | -1.7188 | -14.52 |  | G-F | 8 | 130 | 750 | 0.34907 | 883.4643 | -1.9684 | -5.639 | -14.52
H-G | 0.2032 | 130 | 228.6 | 0.032429 | 0.033856 | -1.044 | -5.8319 |  | H-G | 0.2032 | 130 | 228.6 | 0.032429 | 0.033856 | -1.044 | -5.7732 |  | H-G | 8 | 130 | 750 | 0.34907 | 536.6288 | -1.1956 | -3.4252 | -5.7732
I-H | 0.2032 | 130 | 243.84 | 0.032429 | 0.037134 | -1.1451 | -6.9192 |  | I-H | 0.2032 | 130 | 243.84 | 0.032429 | 0.037134 | -1.1451 | -6.8495 |  | I-H | 8 | 130 | 800 | 0.34907 | 588.582 | -1.3114 | -3.7568 | -6.8495
J-I | 0.2032 | 130 | 121.92 | 0.032429 | 0.084786 | -2.6145 | -31.8704 |  | J-I | 0.2032 | 130 | 121.92 | 0.032429 | 0.084786 | -2.6145 | -31.5494 |  | J-I | 8 | 130 | 400 | 0.34907 | 1343.8896 | -2.9942 | -8.5778 | -31.5494
I-K | 0.2032 | 130 | 228.6 | 0.032429 | 0.044375 | 1.3684 | -9.6203 |  | I-K | 0.2032 | 130 | 228.6 | 0.032429 | 0.044375 | 1.3684 | -9.5234 |  | I-K | 8 | 130 | 750 | 0.34907 | 703.3546 | 1.5671 | 4.4894 | -9.5234
K-E | 0.2032 | 130 | 228.6 | 0.032429 | 0.015937 | 0.49145 | -1.447 |  | K-E | 0.2032 | 130 | 228.6 | 0.032429 | 0.015937 | 0.49145 | -1.4324 |  | K-E | 8 | 130 | 750 | 0.34907 | 252.6129 | 0.56283 | 1.6124 | -1.4324
K-G | 0.2032 | 130 | 243.84 | 0.032429 | 0.02516 | 0.77583 | -3.3674 |  | K-G | 0.2032 | 130 | 243.84 | 0.032429 | 0.02516 | 0.77583 | -3.3334 |  | K-G | 8 | 130 | 800 | 0.34907 | 398.7886 | 0.88851 | 2.5454 | -3.3334
The difference is due to the equations used.

## Delta-Q
Delta Q
https://en.wikipedia.org/wiki/Hardy_Cross_method

## Methods
[1]
https://www.slideshare.net/yourmohsin/pipe-network-analysis

## Ref
[1] | Analysis of water supply distribution networks
Mohsin Siddique
https://www.slideshare.net/yourmohsin/pipe-network-analysis
[2] | CHAPTER 8
WATER DISTRIBUTION SYSTEMS
http://mimoza.marmara.edu.tr/~orhan.gokyay/enve311/ch8.pdf
[3] | Hardy Cross Part 1
by Kenneth Lamb
https://www.youtube.com/watch?v=pjUxSOCRVoo
[4] | Hardy Cross Part 2
by Kenneth Lamb
https://www.youtube.com/watch?v=t35MO1iMp4w
[5] | Hardy Cross Part 3
by Kenneth Lamb
https://www.youtube.com/watch?v=Tg4U3PdzzoY
[6] | Hardy Cross method for solving pipe network problems
I. Nengah Diasta
https://www.academia.edu/27201469/Hardy_Cross_Method_for_Solving_Pipe_Network_Problems
[7] | www.piping-tools.net
Pipes. Flow rate and pressure loss equations_Manning_HazenWilliams_DarcyWeisbach