## 0. Index
				Rev. cjc. 11.08.2016
0		Index
1	PVC pressure	PVC pipe operating pressure					To show hidden sheets, right click on any
2	PVC dim	Standard dimensions and weight of PVC - Polyvinyl Chloride - and CPVC -					sheet tab and select the sheet you want to display.
		Chlorinated Polyvinyl Chloride - pipes according ASTM D1785
		ASTM D1785 "Standard Specification for Poly(Vinyl Chloride) (PVC)
		Plastic Pipe, Schedules 40, 80, and 120"
3	Equation	Standard abbreviated equation (use of outside diameter)
4	P_op. ISO	Operating pressures, using ISO equation (Plastics Pipe Institute)
5	P_op. ASTM	Difference between ASTM and ISO pressure rating methods
6	P_op & Expansion Loops	Operation presssure according ASTM, thermal expansion and expansion loops.
7	Surge for PE pipes	Occasional surge pressures & Negative pressures for PE pipes
8	PVC Data	Material data. Physical properties of rigid PVC and CPVC thermoplastic materials

## 1.- PVC pipe operating pressure
				Rev. cjc. 11.08.2016

Pressure rating for PVC pipes

Pressure rating for a PVC 1120 pipe					Temperature correction					dn
				0,5
Example, according PPI [5]					For temperatures greater than 23 °C, a					0,75
				De-Rating Factor (DRF) shall be applied.					1
Material	PVC 1120					1,25
dn =	2	in				From [2]					1,5
sch =	80	-				Operating	De-Rating					2
				Temp	Factor					2,5
Pipe dimensions					t	DRF					3
de =	Pipe_Imp_PVC_Dext_dn					°C	-					4
de =	60,3	mm				22,8	1					5
s =	Pipe_Imp_PVC_Thickness_dn_sch					26,7	0,88					6
s =	5,5	mm				32,2	0,75					8
				37,8	0,62					10
For PVC 1120					43,3	0,51					12
Table of HDB [4]					48,9	0,4			Hydrostatic Design Stress (HDS = s)					14
Hydrostatic Design Basis					54,4	0,31			s =	sb * DF					16
sb =	4000	psi				60	0,22			sb : Hydrostatic Design Basis [4]
				DF:Design factor forwater at 23 ºC [5]					sch
Design factor forwater at 23 ºC [5]					40
t =	23	°C				As an example, let				Pressure rating					80
DF =	0,5					t =	32	ºC		PR =	2 * s * (s/d)					120
				Value of DRF estimated from above table				s: pipe thickness
Hydrostatic Design Stress (HDS = s)					DRF =	0,75			d: exterior pipe diameter				s/d =	1 / SDR
s =	sb * DF					PR =	2 *sb * DF * (s/d)
sb =	4000	psi				The temperature corrected pressure				PR =	2 * HDB * DF * (s/d)
DF =	0,5					rating is				PR =	2 * HDB * DF / SDR
s =	2000	psi				PRcorrected =	PR * DRF			(See sheet 3. Equation for use of outside diameter
s =	137,9	bar				PR =	25,3	bar		instead of the average diameter)
				DR =	0,75
Pressure rating		[3]				PRcorrected =	19,0	bar		HDB: Hydrostatic Design Basis (sb)
PR =	2 * s * (s/d)					HDS: Hydrostatic Design Stress (s)
s =	137,9	bar					PR: Pressure Rating
s =	5,5	mm					DRF: De-Rating Factor
d =	60,3	mm					DF : Design Factor
PR =	25,3	bar					PRcorrected : By temperature corrected pressure rating

				Rev. cjc. 11.08.2016
PVC pipe operating pressure					Pipe dimensions of PVC and CPVC pipes, shedule 40 and 80

PVC piping pressure ratings are determined using
material ratings by ASTM and PPI (Plastic Pipe					Dimensions of Polyvinyl Chloride (PVC) and Chlorinated Polyvinyl Chloride (CPVC) are defined in ASTM D1785 (Note 1)
Institute) standards and requirements

Pipe pressure ratings are calculated using the					Dimensions in Imperial units					Dimensions in SI units
ISO equation					Sch 40	Sch 80				Sch 40	Sch 80
size 12{ ital "PR"=2 cdot σ cdot { {t} over {d} } } {}					Nominal	Outside	Minimum	Minimum		Nominal	Outside	Minimum	Minimum
				Pipe Size	Diameter	Thickness	Thickness		Pipe Size	Diameter	Thickness	Thickness
				(inches)	(inches)	(inches)	(inches)		in	mm	mm	mm
				1/2	0,84	0,109	0,147		1/2	21,3	2,8	3,7
where					3/4	1,05	0,113	0,154		3/4	26,7	2,9	3,9
PR : Pressure rating (Mpa)					1	1,315	0,133	0,179		1	33,4	3,4	4,5
s : Hydrostatic Design Stress (also HDS) (Mpa)					1 1/4	1,66	0,14	0,191		1 1/4	42,2	3,6	4,9
t : Minimum wall thicknes (mm)					1 1/2	1,9	0,145	0,2		1 1/2	48,3	3,7	5,1
d : Outside pipe diameter (mm)					2	2,375	0,154	0,218		2	60,3	3,9	5,5
				2 1/2	2,875	0,203	0,276		2 1/2	73,0	5,2	7,0
The hydrostatic design stress is calculated as					3	3,5	0,216	0,3		3	88,9	5,5	7,6
size 12{σ= ital "DF" cdot σ rSub { size 8{b} } } {}					4	4,5	0,237	0,337		4	114,3	6,0	8,6
				5	5,563	0,258	0,375		5	141,3	6,6	9,5
				6	6,625	0,28	0,432		6	168,3	7,1	11,0
where					8	8,625	0,322	0,5		8	219,1	8,2	12,7
DF : Design factor					10	10,75	0,365	0,593		10	273,1	9,3	15,1
sb : Hydrostatic design basis (also HDB) (Mpa)					12	12,75	0,406	0,687		12	323,9	10,3	17,4
				14	14	0,438	0,75		14	355,6	11,1	19,1
The design factor (also designed as service factor) for					16	16	0,5	0,843		16	406,4	12,7	21,4
most PVC pipe, with water (tmax = 23 °C) as fluid, is
DF =	0,5
				Note 1
				ASTM D1785 "Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120"

TR-4
TABLE I.A.1 - PVC 1120 MATERIALS1
The following materials carry a recommended HDB of 4,000 psi and a maximum
recommended HDS of 2,000 psi at 73°F (23°C) for water.

alignl { stack { size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { ital "SDR" - 1} } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { { {d} over {s} } - 1} } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { { {d - s} over {s} } } } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {s} over {d - s} } } {} # size 12{ ital "HDS"=σ= ital "HDB" cdot ital "DF"} {} # size 12{ ital "PR"=2 cdot σ cdot { {s} over {d - s} } } {} } } {}
				Polyethylene Pipes (PE)				Pipe expansion. See expansion loops [6]
				Pressure rating for liquid flow surge
				pressurer				The expansion coefficient from PVC is
				l =				5,4E-05	m / (ºC * m)
				Plastic Pipe Insitute recommendation [7]
				Application for
				PE pipes can safely tolerate the				L =				91	m
				commonly observed maximum peak				Dt =				42	ºC
				temporary surge pressure of twice the
				steady state condition.				DL =				L * l * Dt
				L =				91	m
				Long-term strength of PE pipes is not				l =				5,4E-05	m / (ºC * m)
				adversely affected by repeated cyclic				Dt =				42	ºC
				load. Thus, PE pipes are very fatigue				DL =				0,20574	m
				resistant.				DL =				206	mm

## 2.- PVC dim
[2]	PVC and CPVC Pipes - Schedule 40 & 80

	http://www.engineeringtoolbox.com/pvc-cpvc-pipes-dimensions-d_795.html

	Standard dimensions and weight of PVC - Polyvinyl Chloride - and CPVC - Chlorinated Polyvinyl Chloride - pipes according ASTM D1785

	Sponsored Links

	ASTM D1785 "Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120" is manufactured to meet the needs of a broad range of industrial,
	commercial and residential piping systems.

						Poly Vynil Chloride (PVC)
	Typical weight and dimensions of PVC and CPVC pipes are indicated in the table below.					Chlorinated Poly Vynil Chloride (CPVC)

	Insert PVC and CPVC pipes in Sketchup 3D models with the Engineering ToolBox Plugin!

	Note! The dimensions are valid for CPVC Industrial Pipe - not tubing according ASTM D2846 / D2846M "Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC)
	Plastic Hot- and Cold-Water Distribution Systems"

	PVC and CPVC Pipes - Schedule 40					PVC and CPVC Pipes - Schedule 80
	Nominal Pipe Size	Outside Diameter	Minimum Wall Thickness	Nominal Inside Diameter	Weight			Nominal Pipe Size	Outside Diameter	Minimum Wall Thickness	Nominal Inside Diameter	Weight
	(inches)	(inches)	(inches)	(inches)	(lb/ft)			(inches)	(inches)	(inches)	(inches)	(lb/ft)
					PVC	CPVC					PVC	CPVC
	1/2	0,84	0,109	0,622	0,16	0,17		1/2	0,84	0,147	0,546	0,2	0,22
	3/4	1,05	0,113	0,824	0,21	0,23		3/4	1,05	0,154	0,742	0,27	0,3
	1	1,315	0,133	1,049	0,32	0,34		1	1,315	0,179	0,957	0,41	0,44
	1 1/4	1,66	0,14	1,38	0,43	0,46		1 1/4	1,66	0,191	1,278	0,52	0,61
	1 1/2	1,9	0,145	1,61	0,51	0,55		1 1/2	1,9	0,2	1,5	0,67	0,74
	2	2,375	0,154	2,067	0,68	0,74		2	2,375	0,218	1,939	0,95	1,02
	2 1/2	2,875	0,203	2,469	1,07	1,18		2 1/2	2,875	0,276	2,323	1,45	1,56
	3	3,5	0,216	3,068	1,41	1,54		3	3,5	0,3	2,9	1,94	2,09
	4	4,5	0,237	4,026	2,01	2,2		4	4,5	0,337	3,826	2,75	3,05
	5	5,563	0,258	5,047	2,73			5	5,563	0,375	4,813	3,87
	6	6,625	0,28	6,065	3,53	3,86		6	6,625	0,432	5,761	5,42	5,82
	8	8,625	0,322	7,981	5,39	5,81		8	8,625	0,5	7,625	8,05	8,83
	10	10,75	0,365	10,02	7,55	8,24		10	10,75	0,593	9,564	12	13,09
	12	12,75	0,406	11,938	10,01	10,89		12	12,75	0,687	11,376	16,5	18
	14	14	0,438	13,124	11,8			14	14	0,75	12,5	19,3
	16	16	0,5	15	15,43			16	16	0,843	14,314	25,44

	1 lb = 0.4536 kg
	1 ft (foot) = 0.3048 m
	1 in (inch) = 25.4 mm

	PVC - Polyvinyl Chloride

	strong and rigid
	resistant to a variety of acids and bases
	may be damaged by some solvents and chlorinated hydrocarbons
	maximum usable temperature 140oF (60oC)
	usable for water, gas and drainage systems
	not useable in hot water systems

	Operating Temp (°F)	Operating Temp (°C)	De-Rating Factor
	73	22,8	1
	80	26,7	0,88
	90	32,2	0,75
	100	37,8	0,62
	110	43,3	0,51
	120	48,9	0,4
	130	54,4	0,31
	140	60	0,22

	CPVC - Chlorinated Polyvinyl Chloride

	similar to PVC - but designed for water up to approx. 180oF (82oC)

	Operating Temp (°F)	Operating Temp (°C)	De-Rating Factor
	73 - 80	22.8 - 26.7	1
	90	32,2	0,91
	100	37,8	0,82
	110	43,3	0,72
	120	48,9	0,65
	130	54,4	0,57
	140	60	0,5
	150	65,6	0,42
	160	71,1	0,4
	170	76,7	0,29
	180	82,2	0,25
	200	93,3	0,2

## 3. Equation
[3]

## 4.- P_op. ISO
[4]	http://plasticpipe.org/pdf/tr-4-2008a.pdf

	PPI. Thechnical Report TR-4/2008a

						alignl { stack { size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { ital "SDR" - 1} } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { { {d} over {s} } - 1} } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { { {d - s} over {s} } } } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {s} over {d - s} } } {} # size 12{ ital "HDS"=σ= ital "HDB" cdot ital "DF"} {} # size 12{ ital "PR"=2 cdot σ cdot { {s} over {d - s} } } {} } } {}
						alignl { stack { size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { ital "SDR" - 1} } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { { {d} over {s} } - 1} } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {1} over { { {d - s} over {s} } } } } {} # size 12{ ital "PR"=2 cdot ital "HDB" cdot ital "DF" cdot { {s} over {d - s} } } {} # size 12{ ital "HDS"=σ= ital "HDB" cdot ital "DF"} {} # size 12{ ital "PR"=2 cdot σ cdot { {s} over {d - s} } } {} } } {}

						PPI. Thechnical Report TR-4/2008a

## 5.- P_op. ASTM
[5]	tn-28_pressure_differences_between_iso_astm.pdf

						PR =	2 * HDB * DF * (s/d)

						dave =	(d+di)/2
						(d+di)/2 =	(d+(d-2s))/2
						(d+di)/2 =	(2*d - 2*s)/2
						(d+di)/2 =	d-s
						dave =	d-s

						SDR - 1 =	d/s - 1
						SDR - 1 =	d/s - s/s
						SDR - 1 =	(d-s) / s
						1/(SDR-1) =	s / (d-s)
						1/(SDR-1) =	s / dave

	ASTM example					P =	2 * HDB / (SDR - 1) * DF
						www.plasticpipe.org			PE 3408
	P =	DF * 2 * HDB / (SDR - 1) )					HDB =	1600	psi
	P: Pressure rating					PPI TR-4			SDR =	11	-
	DF : Design Factor					DF =	0,5	-
	HDB : Hydrostatic Design Basis (Note 1)					P =	160	psi
	SDR : Standar Dimensions Ratio
						Where SDR standard abbreviation is
	The dersign factor, water applications at 23 ºC, shall be taken as					SDR = de / s
	DF =	0,5					See Ref. 3

	Note 1
	HDB is a Long term strength value developed by testing in accordance with ASTM D 2837
	These values are lisyed in the PPI TR-4 and published at www.plasticpipe.org					alignl { stack { size 12{ ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { ital "SDR" - 1} } } {} # size 12{ ital "PR"":Pr" ital "essure"_ ital "Rating"} {} # size 12{ ital "HDB": ital "Hydrostatic"_ ital "Design"_ ital "Basis"} {} # size 12{ ital "DF": ital "Design"_ ital "Fasctor"} {} # size 12{ ital "SDR":S"tan" ital "dard"_ ital "Dimension"_ ital "Ratio"} {} # size 12{ ital "SDR"= { {d rSub { size 8{e} } } over {s} } } {} # d rSub { size 8{e} } = ital "Average"_ ital "outside"_ ital "diameter" {} # s":min" ital "imum"_ ital "wall"_ ital "thickness" {} # "____________________________" {} # ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { { {d rSub { size 8{e} } } over {s} } - 1} } {} # ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { { {d rSub { size 8{e} } - s} over {s} } } } {} # ital "PR"=2 cdot ital "HDB" cdot { {s} over {d rSub { size 8{e} } - s} } cdot ital "DF" {} # "__________________________" {} # "Pr" ital "essure"_ ital "Design"_ ital "Basis"_ ital "PDB" {} # ital "PDB"=2 cdot ital "HDB" cdot { {s} over {d rSub { size 8{e} } - s} } {} # "___________________________" {} # "Pr" ital "essure"_ ital "Rating"_ ital "PR" {} # ital "PR"= ital "PDB" cdot ital "DF" {} } } {}
			PR: Pressure Rating
			The estimated maximum pressure that the medium in the pipe can exert continuously
			with a high degree of certainty that failure of thepipe will not occur.
	PPI TR-4

						ASTM equation
						size 12{ ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { ital "SDR" - 1} } } {}

						PR: Pressure rating
						HDB: Hydrostatic Design Basis
						DF:Design Factor
						for water at 23 ºC, F = 0.5
						SDR:Standard Dimernsion Ratio
						SDR = de / s
						de: exterior diameter
						s: pipe thickness

	alignl { stack { size 12{ ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { ital "SDR" - 1} } } {} # size 12{ ital "PR"":Pr" ital "essure"_ ital "Rating"} {} # size 12{ ital "HDB": ital "Hydrostatic"_ ital "Design"_ ital "Basis"} {} # size 12{ ital "DF": ital "Design"_ ital "Fasctor"} {} # size 12{ ital "SDR":S"tan" ital "dard"_ ital "Dimension"_ ital "Ratio"} {} # size 12{ ital "SDR"= { {d rSub { size 8{e} } } over {s} } } {} # d rSub { size 8{e} } = ital "Average"_ ital "outside"_ ital "diameter" {} # s":min" ital "imum"_ ital "wall"_ ital "thickness" {} # "__________________________" {} } } {}			alignl { stack { size 12{ ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { { {d rSub { size 8{e} } } over {s} } - 1} } } {} # ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { { {d rSub { size 8{e} } - s} over {s} } } } {} # ital "PR"=2 cdot ital "HDB" cdot { {s} over {d rSub { size 8{e} } - s} } cdot ital "DF" {} } } {}		alignl { stack { size 12{"Pr" ital "essure"_ ital "Design"_ ital "Basis"_ ital "PDB"} {} # size 12{ ital "PDB"=2 cdot ital "HDB" cdot { {s} over {d rSub { size 8{e} } - s} } } {} # "___________________" {} } } {}				alignl { stack { size 12{ ital "PR"=2 cdot ital "HDB" cdot { {s} over {d rSub { size 8{e} } - s} } cdot ital "DF"} {} # "________________________" {} } } {}

						P =	2 * HDB / (SDR - 1) * DF
						alignl { stack { size 12{"Pr" ital "essure"_ ital "Rating"_ ital "PR"} {} # size 12{ ital "PR"= ital "PDB" cdot ital "DF"} {} } } {}				PE 3408
						HDB =	1600	psi
						SDR =	11	-
						DF =	0,5	-
						P =	160	psi
				Design factor for water at 23 ºC
				DF =	0,5					HDS =	HDB * DF
						HDB =	1600	psi
						DF =	0,5	-
	From PPI TR-4					HDS =	800	psi

						P =	2 * HDS / (SDR - 1)

	PE 3408

	PE 3408	According ASTM 1600 nomenclature
	Grade			34
	Density cell class			3
	Slow crack growth class			4	(Acc. ASTM D 3350)
	Hydrostatic Design Stres		HDS =	800	psi
	Hydrostatic Design Basis		HDB =	1600	psi	(Test data)					Design factor forwater at 23 ºC
	Design Factor for water at 23 ºC
			DF =	0,5

						Test data	For water @ 23 ºC
						HDB	HDS
		PPI TR-4, page 14					psi	psi
						DF = 0.5
						CPVC 4120	4000	2000

						POM 21110	2000	1000

						PE 3408	1600	800

## 6.- P_op & Expansion Loops
[6]

					alignl { stack { size 12{σ= { {P cdot \( D rSub { size 8{e} } - s \) } over {2 cdot s} } } {} # σ= { {P cdot \( D rSub { size 8{e} } - s \) } over {2 cdot s} } {} # P= { {2 cdot σ cdot s} over {D rSub { size 8{e} } - s} } {} } } {}

					size 12{σ= { {P cdot \( D rSub { size 8{e} } - s \) } over {2 cdot s} } } {}

					s : hoop stress. This value
					is used as the Hydrostatic
					Design Basis "HDB"

					HDB : Htdrostatic Design Basis.
					Values published by de

					P : Pressure rating (Mpa)
					s : Hydrostatic design stress (Mpa)
					t : Minimum wall thicknes (mm)
					d : Mean diameter (mm)
					size 12{σ= ital "DF" cdot σ rSub { size 8{b} } } {}

					DF : Service Design Factor
					sb : Hydrostatic design basis (Mpa)

					For water at 23 ºC, the PPI recommends
					DF =	0,5

					size 12{P= { {2 cdot σ cdot s} over {D rSub { size 8{e} } - s} } } {}

					CF =	0.00024*M127^2 - 0.04175*M127+1.864

					t
					ºC
					24	1,00	1,00
					27	0,90	0,91
					32	0,75	0,77
					38	0,62	0,62
					43	0,50	0,51
					46	0,45	0,45
					49	0,40	0,39
					52	0,35	0,34
					54	0,30	0,31
					60	0,22	0,22
					66	0,15	0,15

					size 12{ΔL=L cdot λ cdot Δt} {}

					Example
					size 12{ΔL=L cdot λ cdot Δt} {}

					From Table
					y =	0,36	in / (101F * 100 ft)
					y =	0,036	in / (ºF * 100 ft)
					y =	0,00036	in / (ºF * ft)

					DL =	L * l * Dt
					L =	300	ft
					Dt =	75	ºF
					l =	0,00036	in / (ºF * ft)
					DL =	8,1	in

					y =	0,00036	in / (ºF * ft)
					y =	0,009144	mm / (ºF * ft)
					y =	0,0164592	mm / (ºC * ft)
					y =	0,054	mm / (ºC * m)
					l =	5,4E-05	m / (ºC * m)

					Example
					DL =	L * l * Dt
					L =	91,44	m
					l =	5,4E-05	m / (ºC * m)
					Dt =	41,7	ºC
					DL =	0,20574	m
					DL =	205,74	mm
					DL =	8,1	in

					Using Eq. 2.5

					L =	3.5 * ( de * dL )^0.5
					de =	10	in
					dl =	0,675	ft
					L =	9,1	ft
					L =	2,8	m

					Equation [2.5] gives too large values
					There is no deduction nor a reference
					for this equation.

					See calculation below using a checked equation.

					L =
		Expansion loop					Expansion loop length "L"
					size 12{L=0 "." "378" cdot sqrt { { {3 cdot E cdot d cdot f rSub { size 8{ ital "tot"} } } over {σ rSub { size 8{ ital "adm"} } } } } } {}
		Length "L"
		L =	0.378 * ( (3 * E * d * DL) / (sadm) )^0.5
		E =	2,96E+09	Pa
		d =	0,25	m
		DL =	0,206	m
		sadm =	4,96E+07	Pa
		L =	1,1	m
		W =	0,6	m
		Ref. www.piping-tools.net, file Expansion_Loop					Rev. Cjc, 22,01,2013

		PVC
		Modulus of elasticity @ 23 ºC				Expansion
		E =	4,3E+05	psi		DL =	L * l * Dt
		E =	3,0E+06	kPa		L =	91,44	m
					l =	5,4E-05	m / (ºC * m)
		Tensile strength @ 23 ºC				Dt =	41,7	ºC
		s =	7200	psi		DL =	0,20574	m
		s =	5,0E+04	kPa

## 7.- Surge
[7]
	http://www.plasticpipe.org/pdf/chapter06.pdf
	Design of PE Piping Systems
	Chapter 6, page 161

					Pressure rating for liquid flow surge pressure

					For Polyethylene (PE) pipes

					Plastic Pipe Insitute recommendation

					PE pipes can safely tolerate the commonly observed maximum peak
					temporary surge pressure of twice the steady state condition.

					Long-term strength of PE pipes is not adversely affected by repeated
					cyclic load. Thus, PE pipes are very fatigue resistant.

					Occasional surge pressures

					Occasional surge pressures

					alignl { stack { size 12{P rSub { size 8{ ital "tot"={}} } P rSub { size 8{ ital "sustained"} } +P rSub { size 8{ ital "surge"} } } {} # P rSub { size 8{ ital "tot"} } <= 2 cdot ital "PR" rSub { size 8{ ital "temp"_ ital "compensated"} } {} } } {}
					Negative pressures

					Design principles

					alignl { stack { size 12{P rSub { size 8{ ital "tot"={}} } P rSub { size 8{ ital "sustained"} } +P rSub { size 8{ ital "surge"} } } {} # P rSub { size 8{ ital "tot"} } <= 2 cdot ital "PR" rSub { size 8{ ital "temp"_ ital "compensated"} } {} } } {}

	Resin PE pipe material		Resin:	PE4710	alignl { stack { size 12{ ital "PR"=2 cdot { { ital "HDB" cdot ital "DF"} over { ital "SDR" - 1} } } {} # size 12{ ital "PR"":Pr" ital "essure"_ ital "Rating"} {} # size 12{ ital "HDB": ital "Hydrostatic"_ ital "Design"_ ital "Basis"} {} # size 12{ ital "DF": ital "Design"_ ital "Fasctor"} {} # size 12{ ital "SDR":S"tan" ital "dard"_ ital "Dimension"_ ital "Ratio"} {} # size 12{ ital "SDR"= { {d rSub { size 8{e} } } over {s} } } {} # d rSub { size 8{e} } = ital "Average"_ ital "outside"_ ital "diameter" {} # s":min" ital "imum"_ ital "wall"_ ital "thickness" {} # "__________________________" {} } } {}
	Dimensions Ratio		DR =	17
	From Table of TR-4
	HDS =	1000	psi
	HDB =	2000	psi	????
	For water at 23 ºC
	DF =	0,5

	PR =	2 * HDB * DF / (SDR-1)
	HDB =	2000	psi
	DF =	0,5	-
	SDR =	17	-
	PR =	125	psi					PVC 1120
					PVC 2116
	Since the temperature shall remain below 23 ºC,
	no temperature compensation is required.					CPVC 4120
	Thus
	WPR = PR =	125	psi
					PE 1404

					PE 4710

	Pipe´s temperature adjusted PR

## 8.- PVC Data
[8]
	PVC data
	http://www.us.piping.georgefischer.com/go/0B9970F6199943D441223A15E88988AB?action=GF_DocumentDownload&doc_uuid=0B9970F6199943D441223A15E88988AB

					Tensile strength @ 23 ºC
					s =	7200	psi
					s =	5,0E+04	kPa

					Modulus of elesticity @ 23 ºC
					E =	4,3E+05	psi
					E =	3,0E+06	kPa

## PVC 40
1	2	3	4	5	6
2		PVC pipe material		PVC 1120
3		Dimensions according		ASTM D1785 "Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120"
4		Pressure according		ASTM pressure equation
5
6		Schedule 40 PVC Pipe		PVC 1120			PVC 1120
7		Size	de	s	P		Hydrostatic Design Basis
8		in	mm	mm	bar		HDB =	4000	psi
9		1/2	21,34	2,7686	41,1		HDB =	276	bar
10		3/4	26,67	2,8702	33,3		Design Factor for water at 23 ºC
11		1	33,40	3,3782	31,0		DF =	0,5
12		1 1/4	42,16	3,556	25,4		Hydrostatic Design Stress
13		1 1/2	48,26	3,683	22,8		HDS =	HDB * DF
14		2	60,33	3,9116	19,1		HDB =	276	bar
15		2 1/2	73,03	5,1562	21,0		DF =	0,5	-
16		3	88,90	5,4864	18,1		HDS =	137,9	bar
17		4	114,30	6,0198	15,3
18		5	141,30	6,5532	13,4		Application
19		6	168,28	7,112	12,2		dn =	4	in
20		8	219,08	8,4328	11,0		de	114,30	mm
21		10	273,05	9,271	9,7		s =	6,0198	mm
22		12	323,85	10,3124	9,1		SDR =	de / s
							SDR =	19,0
							HDS =	137,9	bar
							P =	2 * HDS / (SDR - 1)
							P =	15,3	bar

## PVC 80
1	2	3	4	5	6
2		PVC pipe material		PVC 1120
3		Dimensions according		ASTM D1785 "Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120"
4		Pressure according		ASTM pressure equation
5
6		Schedule 80 PVC Pipe		PVC 1120			PVC 1120
7		Size	de	s	P		Hydrostatic Design Basis
8		in	mm	mm	bar		HDB =	4000	psi
9		1/2	21,34	3,7338	58,5		HDB =	276	bar
10		3/4	26,67	3,9116	47,4		Design Factor for water at 23 ºC
11		1	33,40	4,5466	43,5		DF =	0,5
12		1 1/4	42,16	4,8514	35,9		Hydrostatic Design Stress
13		1 1/2	48,26	5,08	32,4		HDS =	HDB * DF
14		2	60,33	5,5372	27,9		HDB =	276	bar
15		2 1/2	73,03	7,0104	29,3		DF =	0,5	-
16		3	88,90	7,62	25,9		HDS =	137,9	bar
17		4	114,30	8,5598	22,3
18		5	141,30	9,525	19,9		Application
19		6	168,28	10,9728	19,2		dn =	4	in
20		8	219,08	12,7	17,0		de	114,30	mm
21		10	273,05	15,0622	16,1		s =	8,5598	mm
22		12	323,85	17,4498	15,7		SDR =	de / s
							SDR =	13,4
							HDS =	137,9	bar
							P =	2 * HDS / (SDR - 1)
							P =	22,3	bar

			The standard pipe material designation codes covered by this report are:
			Pipe Material
			Designation Code
			Maximum HDS at
			730F (230C) psi
			HDB at 730F
			(230C) psi
			ASTM
			Specification
			Polyvinyl Chloride (PVC)
			PVC 1120 2,000 4000 D 1785

## PVC_40-80-120
1	2	3	4	5	6	7
2		PVC and CPVC
3		Dimensions according		ASTM D1785
4										1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16
5		PVC pipe dimensions								0,5	0,75	1	1,25	1,5	2	2,5	3	4	5	6	8	10	12	14	16
6				Sch 40	Sch 80	Sch 120
7		NPS	de	s	s	s
8		in	mm	mm	mm	mm
9		0,5	21,34	2,77	3,73	4,32	1,0	0,5		dn (in: 0.5, 0.75, 1, 1.25, 1.5, 2, 2.5, 3, 4, 5, 6, 8, 10, 12, 14, 16. Sch: 40, 80, 120
10		0,75	26,67	2,87	3,91	4,32	2,0	0,75
11		1	33,40	3,38	4,55	5,08	3,0	1		40, 80, 120
12		1,25	42,16	3,56	4,85	5,46	4,0	1,25
13		1,5	48,26	3,68	5,08	5,72	5,0	1,5
14		2	60,33	3,91	5,54	6,35	6,0	2
15		2,5	73,03	5,16	7,01	7,62	7,0	2,5
16		3	88,90	5,49	7,62	8,89	8,0	3
17		4	114,30	6,02	8,56	11,10	9,0	4
18		5	141,30	6,55	9,53	NA	10,0	5
19		6	168,28	7,11	10,97	14,27	11,0	6
20		8	219,08	8,18	12,70	18,24	12,0	8
21		10	273,05	9,27	15,06	NA	13,0	10
22		12	323,85	10,31	17,45	NA	14,0	12
23		14	355,60	11,13	19,05	NA	15,0	14
24		16	406,40	12,70	21,41	NA	16,0	16

		Dimensions
		PVC Schedule 120 pipe shall be manufactured in strict accordance to the requirements of ASTM D1785 for physical dimensions and tolerances
		http://www.harvel.com/technical-support-center/product-specifications/pvc-pipe-schedule-120
		Schedule 120
								OD	s
		Nom. Pipe Size (in)	O.D.	Average I.D.	Min. Wall	Nom. Wt./Ft.	Max. W.P. PSI**	mm	mm
9		1/2"	0,84	0,48	0,17	0,236	1010	21,34	4,318
10		3/4"	1,05	0,69	0,17	0,311	770	26,67	4,318
11		1"	1,315	0,891	0,2	0,464	720	33,40	5,08
12		1-1/4"	1,66	1,204	0,215	0,649	600	42,16	5,461
13		1-1/2"	1,9	1,423	0,225	0,787	540	48,26	5,715
14		2"	2,375	1,845	0,25	1,111	470	60,33	6,35
15		2-1/2"	2,875	2,239	0,3	1,615	470	73,03	7,62
16		3"	3,5	2,758	0,35	2,306	440	88,90	8,89
17		4"	4,5	3,574	0,437	3,713	430	114,30	11,0998
18
19		6"	6,625	5,434	0,562	7,132	370	168,28	14,2748
20		8"	8,625	7,189	0,718	11,277	380	219,08	18,2372

											80
											NPS	de	s
											in	in	in
											1/2	0,84	0,147
											3/4	1,05	0,154
											1	1,315	0,179
											1 1/4	1,66	0,191
											1 1/2	1,9	0,2
											2	2,375	0,218
											2 1/2	2,875	0,276
											3	3,5	0,3
											4	4,5	0,337
											5	5,563	0,375
											6	6,625	0,432
											8	8,625	0,5
											10	10,75	0,593
											12	12,75	0,687
											14	14	0,75
											16	16	0,843

		Related Documents

		CPVC Pipes - Operating and Collapsing Pressure Ratings - Maximum operating and bursting pressures of CPVC - Chlorinated Poly(Vinyl Chloride) - piping systems
		CPVC Pipes - Support Spacing - Support spacing for CPVC pipes
		Cast Iron Soil Pipe - Cast iron soil pipe dimensions
		Comparing Friction Loss in Steel, Copper and Plastic Pipes - Water flow and friction head loss (ft/100 ft) - steel, copper and PVC plastic pipes
		PVC Pipe Schedule 40 - Friction loss and Velocity Diagram - Friction loss (psi/100 ft) and velocity for water flow in plastic PVC pipe schedule 40
		PVC Pipes - Friction Loss and Flow Velocity - Schedule 40 - Water flow in thermoplastic PVC and CPVC pipes Schedule 40 - friction loss (ft/100 ft, psi/100 ft) and flow velocities at dimensions from 1/2 inch to 16 inches
		PVC Pipes - Friction Loss and Flow Velocity - Schedule 80 - Water flow in thermoplastic PVC and CPVC pipes Schedule 80 - friction loss (ft/100 ft, psi/100 ft) and flow velocities at dimensions from 1/2 inch to 16 inches
		PVC Sewer & Drain Pipe - Dimensions of PVC sewer & drain pipes - ASTM D2729
		Pipe Formulas - Pipe and Tube Equations - moment of inertia, section modulus, traverse metal area, external pipe surface and traverse internal area - imperial units
		Plastic Pipes - Friction Head Loss - Friction head loss (ft/100 ft) in plastic pipes, PVC, PP, PE, PEH
		Plastic Pipes and Operating Pressure - ABS, PE, PVC, CPVC, PB, PP and SR
		Steel Pipes Dimensions - ANSI Schedule 40 - Internal and external diameters, areas, weights, volumes and number of threads for schedule 40 steel pipes
		Steel Pipes Dimensions - ANSI Schedule 80 - Internal and external diameters, areas, weights, volumes and number of threads for schedule 80 steel pipes
		Thermoplastic Pipes - Temperature and Maximum Support Spacing - Maximum support spacing PVC, CPVC, PVDF and PP pipes

## Ref
[2]	http://www.engineeringtoolbox.com/pvc-cpvc-pipes-dimensions-d_795.html

[3]	https://www.google.cl/?gws_rd=ssl#q=ASTM+standard+dimension+ratio
	PDF]Chapter 5 - Standard Specifications, Standad Test Methods and ...

	https://plasticpipe.org/pdf/chapter05.pdf
	methods and codes including those issued by ASTM International. (ASTM), American ..... Standard Dimension Ratio (SDR), for a standard Do/t dimension ratio.

[4]	http://plasticpipe.org/pdf/tr-4-2008a.pdf

	PPI. Thechnical Report TR-4/2008a

[5]	http://plasticpipe.org/pdf/tn-28_pressure_differences_between_iso_astm.pdf

[6]

	http://books.google.cl/books?id=rZl6rYd89qoC&printsec=frontcover&hl=es#v=onepage&q&f=false

[7]

	http://www.plasticpipe.org/pdf/chapter06.pdf
	Design of PE Piping Systems
	Chapter 6, page 161

[8]	PVC data
	http://www.us.piping.georgefischer.com/go/0B9970F6199943D441223A15E88988AB?action=GF_DocumentDownload&doc_uuid=0B9970F6199943D441223A15E88988AB