## Chart
				Rev. cjc.28,06.2017
Psychrometric chart for a height above sea level
H =	1500	m.a.s.l.

				Sicro_Absolute_Humidity_tdb_f_H

tdb	Relative humidity f = Sicro_Absolute_Humidity_tdb_f_H [%]
	f = 10%	f = 20%	f = 30%	f = 40%	f = 50%	f = 60%	f = 70%	f = 80%	f = 90%	f = 100%
ºC	10	20	30	40	50	60	70	80	90	100
0	0,0004	0,0009	0,0014	0,0018	0,0023	0,0027	0,0032	0,0036	0,0041	0,0045
5	0,0006	0,0013	0,0019	0,0026	0,0032	0,0039	0,0045	0,0052	0,0058	0,0065
10	0,0009	0,0018	0,0027	0,0036	0,0045	0,0055	0,0064	0,0073	0,0082	0,0092
15	0,0013	0,0025	0,0038	0,0051	0,0063	0,0076	0,0089	0,0102	0,0115	0,0128
20	0,0017	0,0035	0,0052	0,0070	0,0087	0,0105	0,0123	0,0141	0,0159	0,0177
25	0,0023	0,0047	0,0071	0,0095	0,0119	0,0143	0,0168	0,0192	0,0217	0,0242
30	0,0031	0,0063	0,0095	0,0127	0,0160	0,0193	0,0227	0,0260	0,0294	0,0329
35	0,0042	0,0084	0,0127	0,0170	0,0214	0,0259	0,0304	0,0350	0,0396	0,0443
40	0,0055	0,0111	0,0167	0,0225	0,0284	0,0344	0,0405	0,0467	0,0530	0,0595
45	0,0071	0,0144	0,0219	0,0296	0,0374	0,0454	0,0537	0,0621	0,0707	0,0796
50	0,0092	0,0187	0,0285	0,0386	0,0490	0,0597	0,0708	0,0823	0,0941	0,1064
55	0,0118	0,0241	0,0368	0,0501	0,0639	0,0783
60	0,0150	0,0308	0,0474	0,0648
65	0,0190	0,0392	0,0606
70	0,0238	0,0496	0,0774
75	0,0297	0,0625
80	0,0369
85	0,0457
90	0,0563
95	0,0692
100

tdb	Enthalpy h = Sicro_Absolute_Humidity_tdb_ent [kJ/kg]
		h = 10	h = 20	h = 30	h = 40	h = 50	h = 60	h = 70	h = 80	h = 90	h = 100	h = 110	h= 120
ºC	0	10	20	30	40	50	60	70	80	90	100	110	120
0	0,0000	0,0040	0,0080	0,0120
5		0,0020	0,0060	0,0100	0,0139
10		0,0000	0,0040	0,0079	0,0119	0,0159	0,0198	0,0238	0,0278	0,0318	0,0357	0,0397	0,0437
15			0,0020	0,0059	0,0099	0,0138	0,0178	0,0218	0,0257	0,0297	0,0336	0,0376	0,0415
20			0,0000	0,0039	0,0079	0,0118	0,0158	0,0197	0,0236	0,0276	0,0315	0,0355	0,0394
25				0,0020	0,0059	0,0098	0,0137	0,0177	0,0216	0,0255	0,0295	0,0334	0,0373
30				0,0000	0,0039	0,0078	0,0117	0,0157	0,0196	0,0235	0,0274	0,0313	0,0352
35					0,0019	0,0058	0,0097	0,0136	0,0175	0,0214	0,0253	0,0292	0,0331
40					0,0000	0,0039	0,0078	0,0117	0,0155	0,0194	0,0233	0,0272	0,0311
45					0,0019	0,0058	0,0097	0,0136	0,0174	0,0213	0,0252	0,0290
50					0,0000	0,0039	0,0077	0,0116	0,0154	0,0193	0,0232	0,0270
55					0,0019	0,0058	0,0096	0,0135	0,0173	0,0212	0,0250
60					0,0000	0,0038	0,0077	0,0115	0,0153	0,0192	0,0230
65					0,0019	0,0057	0,0095	0,0134	0,0172	0,0210
70					0,0000	0,0038	0,0076	0,0114	0,0152	0,0190
75					0,0019	0,0057	0,0095	0,0133	0,0171
80					0,0000	0,0038	0,0076	0,0113	0,0151
85					0,0019	0,0057	0,0094	0,0132
90					0,0000	0,0038	0,0075	0,0113
95					0,0019	0,0056	0,0094
100					0,0000	0,0037	0,0075
110					0,0000	0,0037
120					0,0000

tdb	Wet bulb temperature twb = Sicro_Absolute_Humidity_tdb_twb_H [ºC]
	twb = 0	twb = 5	twb = 10	twb = 15	twb = 20	twb = 25	twb = 30	twb = 35	twb = 40
ºC	0	5	10	15	20	25	30	35	40
0	0,0045
5	0,0025	0,0065
10		0,0045	0,0092
15		0,0024	0,0071	0,0128
20			0,0051	0,0107	0,0177
25			0,0031	0,0087	0,0156	0,0242
30				0,0066	0,0135	0,0221	0,0329
35				0,0046	0,0115	0,0200	0,0307	0,0443
40				0,0026	0,0094	0,0179	0,0286	0,0421	0,0595
45					0,0074	0,0158	0,0264	0,0399	0,0572
50					0,0053	0,0137	0,0243	0,0377	0,0549
55					0,0033	0,0117	0,0222	0,0355	0,0527
60					0,0096	0,0201	0,0334	0,0504
65					0,0076	0,0180	0,0312	0,0482
70					0,0056	0,0159	0,0291	0,0460
75					0,0139	0,0270	0,0438
80					0,0119	0,0249	0,0416
85					0,0098	0,0228	0,0395
90					0,0078	0,0207	0,0373
95					0,0058	0,0187	0,0352
100					0,0167	0,0331
Psychrometric chart
Dry bulb temperature ºC
Absolute humidity kg-w/kg-da
Relative humidities %
Enthalpies kJ/kg
Wet bulb temperatures ºC

## Psychrometry
				Rev. cjc.28,06.2017
Psychrometric Functions

	Dry bulb temperature		tdb	°C		Absolute humidity		x	kg w/kg da		Dew point temperature		tdp	ºC
	Relative humidity		f	%		Specific volume		v	m3/kg da		Specific enthalpy		ent	kJ/kg da
	Height above sea level		H	m.a.s.l.		Density		r	kg /m3		Wet bulb temperature		twb	ºC

	In the functions to calculate the wet bulb temperature (functions 16, 36, 46 and 56), some limits to the input values of the dry bulb					Maximum values for the input parameters
	temperature, relative humidity and height above sea level have been set to to obtain an acceptable maximum number of iterations.					tdbMax =	96	°C
				f Max =	60	%
	The numbers in square brackets indicate the number of the function in the Basic environment					Hmax =	5300	m.a.s.l.

		Groups
			Group 1			Group 2			Group 3			Group 4			Group 5
			tdb, f , H			tdb, twb, H			tdb, x, H			ent, x, H			tdb, ent, H
tdb	ºC	tdb	32,0	°C	tdb	32,0	°C	tdb	32,0	°C	tdb	32,0	[48]	tdb	32,0	°C
f	%	f	40,0	%	f	40,0	[27]	f	40,0	[37]	f	40,0	[47]	f	40,0	[57]
H	m s.n.m.	H	500,0	m	H	500,0	m	H	500,0	m	H	500,0	m	H	500,0	m
x	kg/kg	x	0,01265	[11]	x	0,0127	[21]	x	0,0127	kg/kg	x	0,0127	kg/kg	x	0,0127	[51]
v	m3/kg	v	0,936	[12]	v	0,936	[22]	v	0,936	[32]	v	0,936	[42]	v	0,936	[52]
r	kg/m3	r	1,082	[13]	r	1,082	[23]	r	1,082	[33]	r	1,082	[43]	r	1,082	[53]		www.piping-tools.net
tdp	ºC	tdp	16,54	[14]	tdp	16,54	[24]	tdp	16,54	[34]	tdp	16,54	[44]	tdp	16,54	[54]		Psychrometric functions_Deductions.xls
ent	kJ/kg	ent	64,4	[15]	ent	64,4	[25]	ent	64,38	[35]	ent	64,38	kJ/kg	ent	64,38	KJ/kg		Rev. cjc. 28.06.2016
twb	ºC	twb	21,41	[16]	twb	21,41	ºC	twb	21,41	[36]	twb	21,41	[46]	twb	21,41	[56]		cjcruz[at]piping-tools.net

## Ref
[1]	Ashrae Handbook
	2005 Fundamentals

[2]	Ashrae Handbook
	1985 Fundamentals

[3]	A quick derivation relating altitude to air pressure
	Version 1.03, 12/22/2004
	2004 Portland State Aerospace Society <http://www.psas.pdx.edu>
	Redistribution allowed under the terms of the GNU General Public License version 2 or later.

	http://psas.pdx.edu/RocketScience/PressureAltitude_Derived.pdf

	www.piping-tools.net
	Psychrometric functions_Deductions.xls
	Rev. cjc. 30.03.2016
	cjcruz[at]piping-tools-net