## Index
				Rev.cjc.29,06,2017

10	Psychrometric table
				twb: wet bulb temperature ºC
11	x = f(tdb, fi,H)			42-43	v = f(ent, x, H)				twb: wet bulb temperature ºC
12-13	v = f(tdb, fi, H)				rho =f(ent, x, H)				H: height above sea level m.a.s.l.
	rho =f(tdb, fi, H)			44	tdp =f(ent, x, H)				x: absolute humidity kg/kg
14	tdp =f(tdb, fi, H)					v: specific volume m3/kg
15	ent =f(tdb, fi, H)			46	twb =f(ent, x, H)				rho: density kg/m3
16	twb =f(tdb, fi, H)			47	fi =f(ent, x, H)				tdp: dew point temperature ºC
				48	tdb =f(ent, x, H)				ent: specific enthalpy kJ/kg
				fi: relative humidity %

21	x = f(tdb, twb, H)			51	x = f(tdb, ent, H)
22-23	v = f(tdb, twb, H)			52-53	v = f(tdb, ent, H)
	rho = f(tdb, twb, H)				rho = f(tdb, ent, H)
24	tdp = f(tdb, twb, H)			54	tdp = f(tdb, ent, H)
25	ent = f(tdb, twb, H)
				56	twb = f(tdb, ent, H)
27	fi = f(tdb, twb, H)			57	fi = f(tdb, ent, H)

32-33	v = f(tdb, x, H)
	rho =f(tdb, x, H)
34	tdp =f(tdb, x, H)
35	ent =f(tdb, x, H)
36	twb =f(tdb, x, H)
37	fi =f(tdb, x, H)

## 10.- Psychrometic table
				Rev.cjc.29,06,2017
Psychrometric Functions

	Dry bulb temperature		tdb	°C		Absolute humidity		x	kg w/kg da		Dew point temperature		tdp	ºC
	Relative humidity		f	%		Specific volume		v	m3/kg da		Specific enthalpy		ent	kJ/kg da
	Height above sea level		H	m.a.s.l.		Density		r	kg /m3		Wet bulb temperature		twb	ºC

	In the functions to calculate the wet bulb temperature (functions 16, 36, 46 and 56), some limits to the input values of the dry bulb					Maximum values for the input parameters
	temperature, relative humidity and height above sea level have been set to to obtain an acceptable maximum number of iterations.					tdbMax =	96	°C
				f Max =	60	%
	The numbers in square brackets indicate the number of the function in the Basic environment					Hmax =	5300	m.a.s.l.

		Groups
			Group 1			Group 2			Group 3			Group 4			Group 5
			tdb, f , H			tdb, twb, H			tdb, x, H			ent, x, H			tdb, ent, H
tdb	ºC	tdb	14,0	°C	tdb	14,0	°C	tdb	14,0	°C	tdb	14,0	[48]	tdb	14,0	°C
f	%	f	31,5	%	f	31,5	[27]	f	31,5	[37]	f	31,5	[47]	f	31,5	[57]
H	m s.n.m.	H	10,0	m	H	10,0	m	H	10,0	m	H	10,0	m	H	10,0	m
x	kg/kg	x	0,00311	[11]	x	0,0031	[21]	x	0,0031	kg/kg	x	0,0031	kg/kg	x	0,0031	[51]
v	m3/kg	v	0,819	[12]	v	0,819	[22]	v	0,819	[32]	v	0,819	[42]	v	0,819	[52]
r	kg/m3	r	1,225	[13]	r	1,225	[23]	r	1,225	[33]	r	1,225	[43]	r	1,225	[53]		www.piping-tools.net
tdp	ºC	tdp	-2,39	[14]	tdp	-2,38	[24]	tdp	-2,39	[34]	tdp	-2,39	[44]	tdp	-2,39	[54]		Psychrometric functions_Deductions.xls
ent	kJ/kg	ent	21,8	[15]	ent	21,9	[25]	ent	21,85	[35]	ent	21,85	kJ/kg	ent	21,85	KJ/kg		Rev. cjc. 30.03.2016
twb	ºC	twb	6,66	[16]	twb	6,66	ºC	twb	6,66	[36]	twb	6,66	[46]	twb	6,66	[56]		cjcruz[at]piping-tools-net

## 11.- x(tdb,f,H)
				Rev.cjc.29,06,2017

11.- Absolute humidity x = f(tdb, f, H)

Input data					Vapor pressure
tdb =	42	°C			Pvap =	fi * Psat
f =	30	%			fi =	0,300	-
H =	680	m			Psat =	0,08208	bar
				Pvap =	0,02462	bar
Atmospheric pressure			[1], Eq. (3)
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588				Absolute humidity			[1], Eq. (8)
H =	680,0	m			x =	0.62198 * Pvap / (Patm - Pvap)
Patm =	0,9342	bar			Pvap =	0,02462	bar
				Patm =	0,93418	bar
Using function 1					x =	0,01684	kg/kg
Saturation pressure at dry bulb temperature			[2]
Psat =	Sicro_Saturated_vapor_pressure_t(tdb) *0.00001				Using function 11
tdb =	42,0	ºC			Sicro_Absolute_Humidity_tdb_f_H
Psat =	0,08208	bar			tdb =	42,0	°C
				f =	30,0	%
Relative humidity					H =	680,0	m
fi =	f / 100				x =	0,01684	kg/kg
f =	30,0	%
fi =	0,300	-

## 12-13.-v&Rho f(tdb,f,H)
				Rev.cjc.29,06,2017

12.- Specific volume v = f(tdb, f, H) and 13.- density r = f(tdb,f , H)

Input data					Vapor pressure				Air gas constant				Density		[1], Eq.(11)
tdb =	35	°C			Pvap =	fi * Psat			Rair =	Rgen / MMair
f =	30	%			fi =	0,300			Rgen:	8314,41	J/(kmol*K)
H =	200	m			Psat =	0,05628	bar		MMair =	28,9645	Kmol/kg
				Pvap =	0,01688	bar		Rair =	287,06	J/(kg*K)		r =	(1/v) * (1 + x)
Atmospheric pressure			[1], Eq. (3)					v =	0,9095	m³/kg da
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588				Absolute humidity		[1], Eq. (8)		Specific volume		[1] Eq.(28)		x =	0,010797	kg/kg
H =	200,0	m			x =	0.62198 * Pvap / (Patm - Pvap)					r =	1,111	kg/m³
Patm =	0,989453234478186	bar			Pvap =	0,01688	bar
				Patm =	0,98945	bar
Using function 1					x =	0,01080	kg/kg
Saturation pressure at dry bulb temperature			[2]					v =	Rair*T/Patm *(1+1.6078*x)			Using function 13
Psat =	Sicro_Saturated_vapor_pressure_t(tdb) *0.00001				Using function 11				Rair =	287,06	J/(kg*K)		r =	Density_twb_f_H
tdb =	35,0	ºC			Sicro_Absolute_Humidity_t_f_H				T =	308,15	K		tdb =	35,0	°C
Psat =	0,05628	bar			tdb =	35,0	°C		Patm =	98.945	Pa		f =	30,0	%
				f =	30,0	%		x =	0,010797	kg/kg		H =	200,0	m
Relative humidity					H =	200,0	m		v =	0,9095	m³/kg da		r =	1,111	kg/m³
fi =	f / 100				x =	0,01080	kg/kg
f =	30,0					Using function 12
fi =	0,300				Absolute dry bulb temperature				v =	Specific_volume_tdb_twb_H
				Tdb =	tdb + 273.15			tdb =	35,0	ºC
				tdb =	35,0	ºC		f	30,0	%
				Tdb =	308,15	K		H =	200,0	m
				v =	0,9095	m³/kg da

## 14.- tdp(tdb,f,H)
				Rev.cjc.29,06,2017
				37.8 / 37.8 / 17.8 / 31.4%
14.- Dew point temperature tdp = f(tdb, f, H)

Data					Relative humidity
tdb =	28,0	°C			fi =	f / 100
f	31,5	%			f =	31,5	%
H =	680,0	m			fi =	0,315	-

Saturation pressure of water at dry bulb temperature					Vapor pressure
tdb =	28,0	°C	[2]		Pvap =	Psat *fi
Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]					Psat =	0,0378	bar
tK =	t + 273.15	°C			fi =	0,315	-
tK =	301,15	K			Pvap =	0,01192	bar
ca =	-5800,22006				Pvap =	1192	Pa
cb =	-5,516256
cc =	-0,048640239
cd =	4,17648E-05				Dew point temperature		Eq. (35), [1, edition 1985], page 6.9
ce =	-1,44521E-08				tdp =	-35.97 - 1.8726 * Ln(Pvap) + 1.1689 * (Ln((Pvap) )^2
cf =	6,5459673				Pvap =	1192	Pa
Psat =	0,0378	bar			tdp =	9,41	°C

				Using function 14
Using function 1			[2]		tdp =	Sicro_Dew_Point_tdb_f_H
Psat =	Sicro_Saturated_vapor_pressure_t				tdb =	28,0	°C					From graphic
t =	28,0	°C			twb =	31,5	%					tdb =	37,8	°C
Psat =	0,0378	bar			H =	680,0	m					f =	31,4	%
				tdp =	9,41	°C					x =	0,0133	g/kg
				tdp =	17,8	°C

## 15.- ent(tdb, f, H)
				Rev.cjc.29,06,2017

15.- Enthalpy ent = f(tdb, f, H)

Input data					Vapor pressure
tdb =	37,8	°C			Pvap =	fi * Psat
f =	31,5	%			fi =	0,315
H =	1420,0	m			Psat =	0,06552	bar
				Pvap =	0,02065	bar
Atmospheric pressure			[1], Eq. (3)
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588				Absolute humidity		[1], Eq. (8)
H =	1420,0	m			x =	0.62198 * Pvap / (Patm - Pvap)
Patm =	0,853893842694139	bar			Pvap =	0,02065	bar
				Patm =	0,85389	bar
Using function 1					x =	0,01541	kg/kg
Saturation pressure at dry bulb temperature			[2]
Psat =	Sicro_Saturated_vapor_pressure_t(tdb) *0.00001				Enthalpy
tdb =	37,8	ºC			ent =	tdb + x * (2501 + 1.805 * tdb)
Psat =	0,06552	bar			tdb =	37,8	ºC
				x =	0,01541	kg/kg
Relative humidity					ent =	77,38	kJ/kg
fi =	f / 100
f =	31,5				Using the function 15
fi =	0,315				x =	Sicro_Enthalpy_tdb_f_H
				tdb =	37,8	°C
				f =	31,5	%
				H =	1420,0	m
				ent =	77,38	kJ/kg

## 16.-twb(tdb,f,H)
				Rev.cjc.29,06,2017

16.- Wet bulb temperature twb = f(tdb, f, H)

Input data					Saturation pressure of water at wet bulb temperature					Wet bulb temperature.		twb =	f(tdb, x, H)
tdb =	42,0	°C			Input
f =	31,5	%			Initially assumed and solution of the wet bulb temperature
H =	1200,0	m			twbold =	26,45	°C
				Psat =(1/100)* Exp(ca / tK + cb + cc*tK + cd*tK ^ 2 + ce * tK ^ 3 + cf*Ln(tK)) [bar]
Atmospheric pressure			'[bar]		tK =	t + 273.15	°C
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588				tK =	299,60	K
H =	1200,0	m			ca =	-5800,22006
Patm =	0,877155697508552	bar			cb =	-5,516256
				cc =	-0,048640239
Using function 1					cd =	4,17648E-05
Saturation pressure at dry bulb temperature			[2]		ce =	-1,44521E-08
Psat =	Sicro_Saturated_vapor_pressure_t(tdb) *0.00001				cf =	6,5459673
tdb =	42,0	ºC			Psat_wb =	0,03454	bar
Psat =	0,08208	bar
				Absolute humidity at saturation and at twb			[1], Eq. (8)
Relative humidity					xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)
fi =	f / 100				Patm =	0,877	bar
f =	31,5	%			Psat_wb =	0,0345	bar
fi =	0,315	-			xsat_twb =	0,025494	kg/kg

Vapor pressure					Wet bulb temperature
Pvap =	fi * Psat				twb = (2501*xsat_twb -tdb - 2501*x - 1.805 * tdb*x ) (2.38* xsat_twb-4.186 x-1)
fi =	0,315				tdb =	42,0	°C
Psat =	0,08208	bar			xsat_twb =	0,02549	kg/kg
Pvap =	0,02587	bar			x =	0,018898	kg/kg			twb =	(2501*xsat_twb -tdb - 2501*x - 1.805 * tdb * x ) / (2.381 * xsat_twb - 4.186 * x - 1 )
				twb =	26,45	ºC			tdb =	42,0	°C
Absolute humidity			[1], Eq. (8)					xsat_twb =	0,015132	kg/kg
x =	0.62198 * Pvap / (Patm - Pvap)				Iteration. Macro uses Goal seek function					x =	0,013046	kg/kg
Pvap =	0,02587	bar			Dtwb =	Abs(twb - twbOld)				twb =	37,08
Patm =	0,87716	bar			Dtwb =	0,000	K
x =	0,01890	kg/kg
				Iteration finished
Using function 11
Sicro_Absolute_Humidity_tdb_f_H					Using function 16
tdb =	42,0	°C			twb =	Sicro_Wet_Bulb_Temperature_tdb_f_H
f =	31,5	%			tdb =	42,0	°C
H =	1200,0	m			f =	31,5	%
x =	0,01890	kg/kg			H =	1200,0	m
				twb =	26,45	ºC

## 21.- x(tdb,twb,H)
				Rev.cjc.29,06,2017
				x = 0.012936 / 37.8 / 23.9 / xsat_twb = 0.01875
21.- Absolute humidity x = f(tdb,twb,H)

Input data
tdb =	25,0	°C			Absolute humidity at saturation and at twb				[1], Eq. (8)
twb =	20,0	°C			xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)
H =	240,0	m			Patm =	0,985	bar
				Psat_wb =	0,0234	bar
Atmospheric pressure			[1], Eq. (3)		xsat_twb =	0,01513	kg/kg
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	240,0	m			Absolute humidity
Patm =	0,985	bar

Saturation pressure of water at wet bulb temperature
Input			[2]
twb =	20,0	°C
Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]
				x =	((2501-2.381*twb)*xsat_twb - (tdb-twb)) / (2501+1.805*tdb-4.186*twb)			[2], Eq. (33)
tK =	t + 273.15	°C			tdb =	25,0	°C
tK =	293,15	K			twb =	20,0	°C
				xsat_wb =	0,01513	kg/kg
ca =	-5800,22006				x =	0,013046	kg/kg
cb =	-5,516256
cc =	-0,048640239				Using the function 21
cd =	4,17648E-05				x =	Sicro_Absolute_Humidity_tdb_twb_H
ce =	-1,44521E-08				tdb =	25,0	°C
cf =	6,5459673				twb =	20,0	°C
				H =	240,0	m
Psat_wb =	0,02339	bar			x =	0,013046	kg/kg

## 22-23.- v&Rho f(tdb,twb,H)
				Rev.cjc.29,06,2017

22.- Specific volume v = f(tdb,twb,H) and 23.- Density r = f(tdb, twb, H)

Input data					Absolute humidity		[2], Eq. (33)		Air gas constant				Density		[1], Eq.(11)
tdb =	37,8	°C			x =((2501-2.381*twb)*xsat_twb - (tdb-twb)) / (2501+1.805*tdb-4.186*twb)				Rair =	Rgen / MMair
twb =	23,9	°C			tdb =	37,8	°C		Rgen:	8314,41	J/(kmol*K)
H =	850,0	m			twb =	23,9	°C		MMair =	28,9645	Kmol/kg
				xsat_wb =	0,02083	kg/kg		Rair =	287,06	J/(kg*K)
Atmospheric pressure			[1], Eq. (3)		x =	0,014991	kg/kg
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588					Specific volume		[1] Eq.(28)		r =	(1/v) * (1 + x)
H =	850,0	m			Using the function 21					v =	0,9987	m³/kg da
Patm =	0,915	bar			x =	Sicro_Absolute_Humidity_tdb_twb_H					x =	0,014991	kg/kg
				tdb =	37,8	°C					r =	1,016	kg/m³
Saturation pressure of water at wet bulb temperature					twb =	23,9	°C
Input			[2]		H =	850,0	m		v =	Rair*T/Patm *(1+1.6078*x)			Using the function 23
twb =	23,9	°C			x =	0,014991	kg/kg		Rair =	287,06	J/(kg*K)		r =	Density_twb_tdb_H
Psat =(1/100)* Exp(ca / tK + cb+cc*tK + cd*tK^ 2 + ce* tK^ 3 + cf*Ln(tK)) [bar]					T =	310,93	K		tdb =	37,8	°C
				Vapor pressure				Patm =	91.522	Pa		twb =	23,9	°C
tK =	t + 273.15	°C					x =	0,014991	kg/kg		H =	850,0	m
tK =	297,038888888889	K					[1], Eq. (8a)		v =	0,9987	m³/kg da		r =	1,016	kg/m³

ca =	-5800,22006					Using the function 22
cb =	-5,516256					v = Sicro_Specific_volume_tdb_twb_H
cc =	-0,048640239					tdb =	37,8	ºC
cd =	4,17648E-05					twb =	23,9	ºC
ce =	-1,44521E-08					H =	850,0	m
cf =	6,5459673				Pvap =	x * Patm / ( 0.62198 + x )			v =	0,9987	m³/kg da
				x =	0,014991	kg/kg
Psat_wb =	0,0297	bar			Patm =	0,915	bar
				Pvap =	0,02154	bar
Absolute humidity at saturation and at twb			[1], Eq. (8)
xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)				Absolute dry bulb temperature
Patm =	0,915	bar			Tdb =	tdb + 273.15
Psat_wb =	0,0297	bar			tdb =	37,8	ºC
xsat_twb =	0,02083	kg/kg			Tdb =	310,93	K

## 24.- tdp(tdb,twb,H)
				Rev.cjc.29,06,2017
				37.8 / 23.9 / 37.8 / 0.01876 / 0.01292 / 17.8 / 31.4%
24.- Dew point temperature tdp = f(tdb, twb,H)

Input data					Absolute humidity			[2], Eq. (33), page 6.9
tdb =	37,8	°C			x = ((2501-2.381*twb)*xsat_twb - (tdb-twb)) / (2501+1.805*tdb-4.186*twb)
twb =	23,9	°C			tdb =	37,8	°C
H =	58,0	m			twb =	23,9	°C
				xsat_twb =	0,01888	kg/kg
Atmospheric pressure			[1], Eq. (3)		x =	0,01307	kg/kg
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	58,0	m			Using the function 21
Patm =	1,006	bar			x =	Sicro_Absolute_Humidity_tdb_twb_H
				tdb =	37,8	°C
Saturation pressure of water at wet bulb temperature					twb =	23,9	°C
			[2]		H =	58,0	m
twb =	23,9	°C			x =	0,01307	kg/kg
Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]
tK =	t + 273.15	°C			Water vapor partial pressure.			[1], Eq. (8a)
tK =	297,038888888889	K			Pvap =	x * Patm / ( 0.62198 + x )
ca =	-5800,22006				x =	0,01307	kg/lg
cb =	-5,516256				Patm =	1,006	bar
cc =	-0,048640239				Pvap =	0,02071	bar
cd =	4,17648E-05				Pvap =	2071	Pa
ce =	-1,44521E-08
cf =	6,5459673				Dew point temperature			Eq. (35), [2], page 6.9
Psat_wb =	0,0297	bar			tdp =	-35.97 - 1.8726 * Ln(Pvap) + 1.1689 * (Ln((PvaP) )^2
				Pvap =	2071	Pa
Using function 1			[2]		tdp =	17,88	°C
Psat_wb =	Sicro_Saturated_vapor_pressure_t
twb =	23,9	°C			Using function 24
Psat_wb =	0,0297	bar			tdp =	Sicro_Dew_Point_tdb_twb_H(tdb, twb, H)
				tdb =	37,8	°C
Absolute humidity at saturation and at twb			[1], Eq. (8)		twb =	23,9	°C
xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)				H =	58,0	m
				tdp =	17,88	°C
Patm =	1,006	bar
Psat =	0,0297	bar
xsat_twb =	0,01888	kg/kg					Using function 24
				From graphic			Sicro_Dew_Point_tdb_twb_H
				tdb =	37,8	°C	tdb =	37,8	°C
				f =	31,4	%	twb =	23,9	°C
				x =	58,0	g/kg	H =	58,0	m
				tdp =	17,8	°C	tdp =	17,88	°C

				Function DewPoint(p, W)
				'
				' DewPoint Macro
				' Macro recorded 9/23/2003 by Skavanaugh
				'
				pw = (p * W) / (0.62198 + W)

				alpha = Log(pw)

				C14 =	100,45
				C15 =	33,193
				C16 =	2,319
				C17 =	0,17074
				C18 =	1,2063

				DewPoint =	C14 + C15 * alpha + C16 * alpha ^ 2 + C17 * alpha ^ 3 + C18 * (pw) ^ 0.1984

				End Function

				tdb =	100	°F	37,8
				twb =	75	°F	23,9
				H =	11	ft
				W =	#NAME?	lb/lb

				p =	14.696 * (1 - 0.0000068753 * Elevation) ^ 5.2559
				p =	14,690	psi

				pw =	(p * W) / (0.62198 + W)
				p =	14,690	psi
				W =	#NAME?	lb/lb
				pw =	#NAME?	psi
				alpha =	Ln(pw) =	#NAME?

				tdp =	C14 + C15 * alpha + C16 * alpha ^ 2 + C17 * alpha ^ 3 + C18 * (pw) ^ 0.1984
				tdp =	#NAME?	°F
				tdp =	#NAME?	°C

## 25.- ent(tdb,twb,H
				Rev.cjc.29,06,2017

25.- Enthalpy ent = f(tdb, twb,H)

Data					Absolute humidity at saturation and at twb				[1], Eq. (8)
tdb =	37,8	°C				xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)
twb =	23,9	°C				Patm =	0,877	bar
H =	1200,0	m				Psat =	0,0297	bar
				xsat_twb =	0,02176	kg/kg

Atmospheric pressure				[1], Eq. (3)		Absolute humidity
Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	1200,0	m
Patm =	0,877	bar

Saturation pressure of water at wet bulb temperature				[2]
Input
twb =	23,9	°C				x =	((2501-2.381*twb)*xsat_twb - (tdb-twb)) / (2501+1.805*tdb-4.186*twb)			[2], Eq. (33)
Psat =(1/100)*Exp(ca tK+cb+cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]					tdb =	37,8	°C
				twb =	23,9	°C
tK =	t + 273.15	°C				xsat_wb =	0,02176	kg/kg
tK =	297,038888888889	K				x =	0,0159162	kg/kg

ca =	-5800,22006					Using the function 21
cb =	-5,516256					x =	Sicro_Absolute_Humidity_tdb_twb_H
cc =	-0,048640239					tdb =	37,8	°C
cd =	4,17648E-05					twb =	23,9	°C
ce =	-1,44521E-08					H =	1200,0	m
cf =	6,5459673					x =	0,0159162	kg/kg

Psat_wb =	0,0297	bar				Enthalpy		[2], Eq. (30)
				h =	tdb + x * (2501 + 1.805 * tdb)
				tdb =	37,8	°C
[2], Eq. (30), page 6.9					x =	0,0159162	kg/kg
				h =	78,67	kJ/kg

h =	t + x * (2501 + 1.805 * t)					Using the function 25
h: specific enthalpy		[kJ/kg da]				ent =	Sicro_Enthalpy_tdb_twb_H
t: dry bulb temperature		[°C]				tdb =	37,778	°C
x: absolute humidity		[kg/lg]				twb =	23,9	°C
				H =	1200,0	m
				h =	78,67	kJ/kg

## 27.-f(tdb,twb,H)
				Rev.cjc.29,06,2017
27.- Relative humidity f = f(tdb, twb,H)

				Vapor pressure				Saturation pressure of water vapor [2]				Water vapor partial pressure [1], Eq. (8a)
	Input data					tdb =	40,0	°C		Pvap =	x * Patm / ( 0.62198 + x )
	tdb =	40,0	°C					Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]				Pvap =	0,019518397800991	bar
	twb =	23,9	°C					tK =	t + 273.15	°C
	H =	250,0	m.a.s.l.					tK =	313,2	K		Air partial pressure
				ca =	-5800,22006			Pair =	Patm - Pvap
	Relative humidity					cb =	-5,516256			Pair =	0,964056935659458	bar
				cc =	-0,048640239
				cd =	4,17648E-05			Relative humidity		[1], Eq. (8b)
				ce =	-1,44521E-08			f =	(x / 0.62198) * (Pair/Psat) * 100
				cf =	6,5459673			x =	0,0126
				Psat =	0,0738	bar		Pair =	0,964056935659458	bar
				Psat =	0,0738	bar
				Atmospheric pressure		[1], Eq. (3)		f =	26,4	%
				Patm =	1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
				Patm =	0,983575333460449	bar		Using the function 27
				Sicro_Relative_Humidity_tdb_twb_H
				Using the function 21				tdb =	40,0	°C
				Sicro_Absolute_Humidity_tdb_twb_H				twb =	23,9	°C
				tdb =	40,0	ºC		H =	250,0	m.a.s..l.
				twb =	23,9	ºC		f =	26,4	%
				H =	250,0	m.a.s.l.
			[1], Eq. (8b)					x =	0,01259	kg/kg

## 32-33.- v&Rho f(tdb,x,H)
				Rev.cjc.29,06,2017

32.- Specific volume and 33.- density

				Using the function 11				33.- Density		[1], Eq.(11)
Input data					Sicro_Absolute_Humidity_tdb_f_H
tdb =	25,0	°C			tdb =	25,0	°C
x	0,01294	kg/kg			f =	64,2	%
H =	125,0	m			H =	125,0	m
				x =	0,01294	kg/kg
Atmospheric pressure		'[bar]	[1], Eq. (3)					r =	(1/v) * (1 + x)
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588					Absolute dry bulb temperature				v =	0,875	m³/kg da
H =	125,0	m			Tdb =	tdb + 273.15			x =	0,012943	kg/kg
Patm =	0,99832	bar			tdb =	25,0	ºC		r =	1,157	kg/m³
				Tdb =	298,15	K
Saturation pressure at dry bulb temperature			[2]					Using the function 33
Psat =	Sicro_Saturated_vapor_pressure_t(tdb *0.00001				Air gas constant				r =	Sicro_Density_twb_x_H
tdb =	25,0	ºC			Rair =	Rgen / MMair			tdb =	25,0	°C
Psat =	0,03169	bar			Rgen:	8314,41	J/(kmol*K)		x =	0,0129	kg/kg
				MMair =	28,9645	Kmol/kg		H =	125,0	m
Relative humidity			[1], Eq. (8b)		Rair =	287,06	J/(kg*K)		r =	1,157	kg/m³
f =	(Patm/Psat) * (x /(0.62198 + x ) )
Patm =	0,99832	bar			Specific volume		[1] Eq.(26), page 6.9
Psat =	0,03169	bar
x =	0,01294	kg/kg
f =	0,642	-
f =	64,2	%
				v =	Rair*T/Patm *(1+1.6078*x)
Vapor pressure					Rair =	287,06	J/(kg*K)
Pvap =	fi * Psat				T =	298,15	K
fi =	0,642				Patm =	99.832	Pa
Psat =	0,03169	bar			x =	0,012943	kg/kg
Pvap =	0,02035	bar			v =	0,875	m³/kg da

Absolute humidity			[1], Eq. (8)		Using the function (32)
x = 0.62198 * Pvap / (Patm - Pvap)					v =	Specific_volume_tdb_x_H
Pvap =	0,02035	bar			tdb =	25,0	ºC
Patm =	0,99832	bar			x =	0,0129	kg/kg
x =	0,01294	kg/kg			H =	125,0	m
				v =	0,875	m³/kg da

## 34. tdp(tdb,x,H)
				Rev.cjc.29,06,2017

34.- Dew point temperature tdp = f(x, H)

Input data					Dew point temperature			Eq. (35), [2], page 6.9
x	0,01294	kg/kg				tdp =	-35.97 - 1.8726 * Ln(Pvap) + 1.1689 * (Ln((PvaP) )^2
H =	120,0	m				Pvap =	2036	Pa
				tdp =	17,62	°C
Atmospheric pressure		'[bar]	[1], Eq. (3)
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588					Using the function 34
H =	120,0	m				tdp =	Sicro_Dew_Point_x_H( x, H)
Patm =	0,99892	bar				x =	0,01294	°C
				H =	120,0	m
Water vapor partial pressure.					tdp =	17,62	°C

Pvap =	x * Patm / ( 0.62198 + x )		[1], Eq. (8a)
x =	0,01294	kg/lg
Patm =	0,999	bar
Pvap =	0,02036	bar
Pvap =	2036	Pa

## 35.- ent(tdb,x,H)
				Rev.cjc.29,06,2017

35.- Enthalpy ent = ent(tdb, x)

Input data
tdb =	52,0	°C
x =	0,01200	kg/kg
H =	4000,0	m

Enthalpy			[2], Eq. (30)
ent =	tdb + x * (2501 + 1.805 * tdb)
tdb =	52,0	°C
x =	0,0120000	kg/kg
ent =	83,14	kJ/kg

Using the function 35
Sicro_Enthalpy_tdb_x
H =	Sicro_Enthalpy_tdb_x_H(tdb, x, H)			Note: The enthalpy does not depend on the height above sea level
tdb =	52,000	°C		The function could be modified eliminating thso input.
x =	0,01200	kg/kg
H =	4000,0	m.a.s.l.
ent =	83,14	kJ/kg

[2], Eq. (30), page 6.9

h =	t + x * (2501 + 1.805 * t)
h: specific enthalpy		[kJ/kg da]
t: dry bulb temperature		[°C]
x: absolute humidity		[kg/lg]

## 36.- twb(tdb,x,H)
				Rev.cjc.29,06,2017

36.- Wet bulb temperature twb = twb(tdb, x, H)

Input data					Absolute humidity at saturation and at twb
tdb =	20,0	°C			xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)			[1], Eq. (8)		Wet bulb temperature.		twb =	f(tdb, x, H)
x	0,012	kg/kg			Patm =	0,846	bar
H =	0,0	m			Psat_wb =	0,01818	bar
				xsat_twb =	0,013670	kg/kg
Using the function 36
twb =	Sicro_Wet_Bulb_temperature_tdb_x_H
tdb =	20,0	°C			Wet bulb temperature				[2], Eq. (33)
x =	0,01200	%			twb = (2501*xsat_twb -tdb - 2501*x - 1.805 * tdb*x ) (2.38* xsat_twb-4.186 x-1)
H =	1500,0	m			tdb =	20,0	°C
twb =	16,0	ºC			xsat_twb =	0,01367	kg/kg
				x =	0,012000	kg/kg
				twb =	15,974	|C
Atmospheric pressure		'[bar]	[1], Eq. (3)
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588					Iterate until assumed twb is near to calculated twb
H =	1500,0	m
Patm =	0,84556	bar

Saturation pressure of water at wet bulb temperature					twb =	(2501*xsat_twb -tdb - 2501*x - 1.805 * tdb * x ) / (2.381 * xsat_twb - 4.186 * x - 1 )
Assumed Input			[2]					tdb =	20,0	°C
twb =	16,00	°C					xsat_twb =	0,015132	kg/kg
Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]					x =	0,013046	kg/kg
tK =	t + 273.15	°C					twb =	14,98
tK =	289,15	K
ca =	-5800,22006
cb =	-5,516256
cc =	-0,048640239
cd =	4,17648E-05
ce =	-1,44521E-08
cf =	6,5459673
Psat_wb =	0,01818	bar

## 37.- f(tdb,x,H)
				Rev.cjc.29,06,2017

37.- Relative humidity f = f(tdb , x, H)

Input data
tdb =	35,0	°C
x	0,01294	kg/kg
H =	450,0	m

Atmospheric pressure		'[bar]	[1], Eq. (3)
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	450,0	m
Patm =	0,96035	bar

Saturation pressure at dry bulb temperature			[2]
Psat =	Sicro_Saturated_vapor_pressure_t(tdb *0.00001
tdb =	35,0	|C
Psat =	0,05628	bar

Relative humidity			[1], Eq. (8b)
f =	(Patm/Psat) * (x /(0.62198 + x ) )
Patm =	0,96035	bar
Psat =	0,05628	bar			x =	0.62198 * Pvap / (Patm - Pvap)
x =	0,01294	kg/kg
f =	0,348	-

Using the function 37
f =	Sicro_Relative_Humidity_tdb_x_H
tdb =	35,0	°C
x	0,01294	kg/kg
H =	450,0	m
f =	34,8	%

## 42-43.- v&Rho f(ent,x,H)
				Rev.cjc.29,06,2017

42.- Specific volume v = v(ent, x, H) and 43.- density Rho = f(ent, x, H)

ent =	65,00	kJ/kg					7.- Density		[1], Eq.(11)
x	0,01294	kg/kg		Relative humidity		[1], Eq. (8b)		Absolute dry bulb temperature
H =	3,4	m		f =	(Patm/Psat) * (x /(0.62198 + x ) )			Tdb =	tdb + 273.15
				Patm =	1,009	bar		tdb =	31,9	ºC
				Psat =	0,04727	bar		Tdb =	305,03	K
Dry bulb temperature		[1], Eq. (32)		x =	0,01294	kg/kg
tdb =	(h - x*2501) / (1.805*x+1)			f =	0,435	-		Air gas constant				r =	(1/v) * (1 + x)
h =	65,0	kJ/kg		f =	43,5	%		Rair =	Rgen / MMair			v =	0,885	m³/kg da
x =	0,0129433	kg/kg					Rgen:	8314,41	J/(kmol*K)		x =	0,012899	kg/kg
tdb =	31,9	kJ/kg		'Vapor presure				MMair =	28,9645	Kmol/kg		r =	1,144	kg/m³
				Pvap =	fi * Psat			Rair =	287,06	J/(kg*K)
Using the function 48				fi =	0,435					Using the function 43
Sicro_Dry_Bulb_Temperature_ent_x				Psat =	0,04727	bar		Specific volume		[1] Eq.(26), page 6.9		r =	Sicro_Density_ent_x_H(ent, x, H)
h =	65,0000	kJ/kg		Pvap =	0,02058	bar					tdb =	65,0	kJ/kg
x =	0,0129	kg/kg					x =	0,0129	kg/kg
tdb =	31,9	m		'Absolute humidity		[1], Eq. (8)					H =	3,4	m
				x = 0.62198 * Pvap / (Patm - Pvap)					r =	1,148	kg/m³
Atmospheric pressure		[1], Eq. (3)		Pvap =	0,02058	bar		v =	Rair*T/Patm *(1+1.6078*x)
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588				Patm =	1,00943	bar		Rair =	287,06	J/(kg*K)
H =	31,9	m		x =	0,01294	kg/kg		T =	305,03	K
Patm =	1,009	bar					Patm =	100.943	Pa
				Using the function 11				x =	0,012943	kg/kg
Saturation pressure at dry bulb temperature				Sicro_Absolute_Humidity_tdb_f_H				v =	0,885	m³/kg da
		[2]		tdb =	31,9	°C
Psat = Sicro_Saturated_vapor_pressure_t(tdb *0.00001				f =	43,5	%		Using the function (42)
tdb =	31,9	|C		H =	3,4	m		v =	Specific_Volume_ent_x_H(ent, x, H)
Psat =	0,04727	bar		x =	0,01290	kg/kg		ent =	65,0	kJ/kg
				x =	0,0129	kg/kg
				H =	3,4	m
				v =	0,882	m³/kg da

				Density		[1], Eq.(11)

				ent =	2501 * x + tdb * (1.006+1.86*x)
				x =	0,0129	kg/kg
				tdb =	31,9
				ent =	65,21	kJ/kg

## 44.- tdp(ent,x,H)
				Rev.cjc.29,06,2017

44.- Dew point temperature tdp = tdp( x, H)

Data
x	0,01294	kg/kg			Dew point temperature			Eq. (35), [2], page 6.9
H =	120,0	m			tdp =	-35.97 - 1.8726 * Ln(Pvap) + 1.1689 * (Ln((PvaP) )^2
				Pvap =	2036	Pa
Atmospheric pressure		[1], Eq. (3)			tdp =	17,62	°C
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	120,0	m			Using the function 44
Patm =	0,999	bar			tdp =	Sicro_Dew_Point_x_H(x, H)
				x =	0,01294	°C
Water vapor partial pressure.					H =	120,0	m
Pvap =	x * Patm / ( 0.62198 + x )		[1], Eq. (8a)		tdp =	17,62	°C
x =	0,01294	kg/lg
Patm =	0,999	bar
Pvap =	0,02036	bar
Pvap =	2036	Pa

## 46.- wbt(ent,x,H)
				Rev.cjc.29,06,2017

46.- Wet bulb temperature twb = twb(ent, x, H)

				Absolute humidity at saturation and at twb
Input data				xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)				Wet bulb temperature.		twb =	f(tdb, x, H)
ent	52,0	kJ/kg		Patm =	1,011	bar
x	0,01294	kg/kg		Psat_wb =	0,0297	bar
H =	3,4	m		xsat_twb =	0,018795	kg/kg

Dry bulb temperature				Wet bulb temperature
tdb =	(h - x*2501) / (1.805*x+1)			twb = (2501*xsat_twb -tdb - 2501*x - 1.805 * tdb*x ) (2.38* xsat_twb-4.186 x-1)
h =	52,0	kJ/kg		tdb =	19,2	°C
x =	0,0129	kg/kg		xsat_twb =	0,01879	kg/kg
tdb =	19,2	kJ/kg		x =	0,012943	kg/kg
				twb =	4,95	|C
Using the function 48
Sicro_Dry_Bulb_Temperature_ent_x				Using the function 46
h =	52,0000	kJ/kg		twb =	Sicro_Wet_Bulb_Temperature_ent_x_H
x =	0,0129	kg/kg		tdb =	52,0	°C
tdb =	19,2	m		x =	0,01294	%
				H =	3,4	m
Atmospheric pressure		[1], Eq. (3)		twb =	18,39	ºC
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	19,2	m
Patm =	1,011	bar

Saturation pressure of water at wet bulb temperature
Input					20,00	°C
twb =	23,89	°C
Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]					twb =	(2501*xsat_twb -tdb - 2501*x - 1.805 * tdb * x ) / (2.381 * xsat_twb - 4.186 * x - 1 )
				tdb =	52,0	°C
tK =	t + 273.15	°C					xsat_twb =	0,015132	kg/kg
tK =	297,038888888889	K					x =	0,013046	kg/kg
				twb =	47,13
ca =	-5800,22006
cb =	-5,516256
cc =	-0,048640239
cd =	4,17648E-05
ce =	-1,44521E-08
cf =	6,5459673

Psat_wb =	0,02965	bar

## 47.- f(ent,x,H)
				Rev.cjc.29,06,2017

47.- Relative humidity f = f(ent, x, H)

Input data				Saturation pressure at dry bulb temperature
ent =	65,0	kJ/kg		Psat = Sicro_Saturated_vapor_pressure_t(tdb *0.00001
x	0,01294	kg/kg		tdb =	31,9	|C
H =	3,4	m		Psat =	0,04727	bar

Dry bulb temperature				Relative humidity
tdb =	(ent - x*2501) / (1.805*x+1)			f = (Patm/Psat) * (x /(0.62198 + x ) )
h =	65,0	kJ/kg		Patm =	1,0128	bar
x =	0,0	kg/kg		Psat =	0,04727	bar
tdb =	31,9	kJ/kg		x =	0,01294	kg/kg
				f =	0,437	-

Using the function 48				Using the function 47
Sicro_Dry_Bulb_Temperature_ent_x				f =	Sicro_Relative_Humidity_ent_x_H(ent, x, H)
h =	65,0000	kJ/kg		ent =	65,0	kJ/kg
x =	0,0129	kg/kg		x	0,01294	kg/kg
tdb =	31,9	m		H =	3,4	m
				f =	43,7	%
Atmospheric pressure		'[bar]
Patm = 1.01325 * (1 - 0.0000225577 * H) ^ 5.25588
H =	3,4	m
Patm =	1,0128	bar

## 48.- tdb(ent,x,H)
				Rev.cjc.29,06,2017

48.- Dry bulb temperature tdb = tdb(ent, x, H)

Data
h =	70,0	kJ/kg
x =	0,01294	kg/kg
H =	3,4	m

Dry bulb temperature			[1], Eq. (32)
tdb =	(h - x*2501) / (1.805*x+1)
h =	70,0	kJ/kg
x =	0,0129433	kg/kg
tdb =	36,8	kJ/kg

Using the function 48					[2], Eq. (30), page 6.9
ent =	Sicro_Dry_Bulb_Temperature_ent_x
h =	70,0000	kJ/kg			h =	t + x * (2501 + 1.805 * t)
x =	0,0129	kg/kg			h: specific enthalpy		[kJ/kg da]
tdb =	36,8	m			t: dry bulb temperature		[°C]
				x: absolute humidity		[kg/lg]

## 51.- x(tdb,ent,H)
				Rev.cjc.29,06,2017

51.- Absolute humidity x = x(tdb, ent)

Imput data	(Not a function of H)
tdb =	35,0	°C
ent =	71,03	kJ/kg

Absolute humidity
x =	(ent - tdb) / (2501 + 1.805*tdb )		[1], Eq. (32b)
ent =	71,03	kJ/kg
tdb =	35,0	ºC
x =	0,014052	kg/kg

Using function 51
x =	Sicro_Absolute_Humidity_tdb_ent(tdb, ent)			Independet of the height above sea level
tdb =	35,0	°C
ent =	71,0	kJ/kg
x =	0,01405	kg/kg

## 52-53.- v&Rho f(tdb,ent,H)
				Rev.cjc.29,06,2017

52.- Specific volume v = v(tdb, ent, H) and 53.- density r = r(tdb, ent, H)

Input data				Relative humidity		[1], Eq. (8b)		Air gas constant				Using the function 52
tdb =	18,00	ºC		f =	(Patm/Psat) * (x /(0.62198 + x ) )			Rair =	Rgen / MMair			v = Sicro_Specific_Volume_tdb_ent_H
ent =	71,03	kJ/kg		Patm =	1,01285	bar		Rgen:	8314,41	J/(kmol*K)		tdb =	37,78	ºC
H =	3,4	m		Psat =	0,02064	bar		MMair =	28,9645	Kmol/kg		ent =	71,0	kJ/kg
				x =	0,02093	kg/kg		Rair =	287,06	J/(kg*K)		H =	3,4	m
Atmospheric pressure		[1], Eq. (3)		f =	1,597	-					v =	0,900	m³/kg da
Patm= 1.01325 * (1-0.0000225577 *H) ^ 5.25588				f =	159,7	%		Specific volume		[1] Eq.(26), page 6.9
H =	3,4	m					53.- Density		[1], Eq.(26), page 6.8
Patm =	1,01285	bar		'Vapor presure
				Pvap =	fi * Psat
Saturation pressure at dry bulb temperature				fi =	1,597
		[2]		Psat =	0,02064	bar		v =	Rair*T/Patm *(1+1.6078*x)
Psat = Sicro_Saturated_vapor_pressure_t(tdb *0.00001				Pvap =	0,03298	bar		Rair =	287,06	J/(kg*K)
tdb =	18,0	|C					T =	291,15	K		r =	(1/v) * (1 + x)
Psat =	0,02064	bar		Absolute dry bulb temperature				Patm =	101.285	Pa		v =	0,853	m³/kg da
				Tdb =	tdb + 273.15			x =	0,020932	kg/kg		x =	0,020932	kg/kg
Absolute humidity		[1], Eq. (32b)		tdb =	18,0	ºC		v =	0,853	m³/kg da		r =	1,197	kg/m³
x =	(ent - tdb) / (2501 + 1.805*tdb )			Tdb =	291,15	K
ent =	71,03	kg/kg					Using the function 53
tdb =	18,0	ºC					Rho = Sicro_Density_tdb_ent_H(tdb, ent, H)
x =	0,020932	kg/kg					tdb =	37,78	ºC
				ent =	71,0	kJ/kg
				H =	3,4	m
				r =	1,126	kg/m³

## 54.- tdp(tdb,ent,H)
				Rev.cjc.29,06,2017

54.- Dew point temperature tdp = tdp(tdb, ent, H)

Data					Dew point temperature			Eq. (35), [2], page 6.9
tdb =	21,0	ºC			tdp =	-35.97 - 1.8726 * Ln(Pvap) + 1.1689 * (Ln((PvaP) )^2
ent =	71,0	kJ/kg			Pvap =	3112	Pa
H =	3,4	m			tdp =	24,58	°C

Absolute humidity			[1], Eq. (32b)		Using the function 54
x =	(ent - tdb) / (2501 + 1.805*tdb )				tdp =	Sicro_Dew_Point_tdb_ent_H(tdb,ent, H)
ent =	71,03	kg/kg			tdb =	21,0	°C
tdb =	21,0	ºC			ent =	71,03163	kJ/kg
x =	0,019706	kg/kg			H =	3,4	m
				tdp =	24,58	°C
Atmospheric pressure			[1], Eq. (3)
Patm= 1.01325 * (1-0.0000225577 *H) ^ 5.25588
H =	0,0	m
Patm =	1,01325	bar

Water vapor partial pressure.			[1], Eq. (8a)
Pvap =	x * Patm / ( 0.62198 + x )
x =	0,01971	kg/lg
Patm =	1,013	bar
Pvap =	0,03112	bar
Pvap =	3112	Pa

## 56.- twb(tdb,ent,H)
				Rev.cjc.29,06,2017

56.- Wet bulb temperature twb = twb(tdb, ent, H)

Input data					Absolute humidity at saturation and at twb				[1], Eq. (8)		Wet bulb temperature.		twb =	f(tdb, x, H)
tdb =	23,0	°C			xsat_twb =	0.62198 * Psat_twb / (Patm - Psat_twb)
ent =	71,03	kg/kg			Patm =	1,013	bar
H =	3,4	m			Psat_wb =	0,0297	bar
				xsat_twb =	0,018751	kg/kg
Absolute humidity			[1], Eq. (32b)
x =	(ent - tdb) / (2501 + 1.805*tdb )				Wet bulb temperature
ent =	71,03	kg/kg			twb = (2501*xsat_twb -tdb - 2501*x - 1.805 * tdb*x ) (2.38* xsat_twb-4.186 x-1)
tdb =	23,0	ºC			tdb =	23,0	°C
x =	0,018891	kg/kg			xsat_twb =	0,01875	kg/kg
				x =	0,018891	kg/kg
Using the function 51					twb =	23,33	|C
	Sicro_Absolute_Humidity_tdb_ent(tdb, ent)
tdb =	23,0	°C			Using the function 56
ent =	71,0	kg/kg			twb =	Sicro_Wet_Bulb_Temperature_ent_x_H
H =	3,4	m			tdb =	23,0	°C
x =	0,01889	m			ent	71,03163	%
				H =	3,4	m
Atmospheric pressure			[1], Eq. (3)		twb =	23,73	ºC
Patm= 1.01325 * (1-0.0000225577 *H) ^ 5.25588
H =	0,0	m					twb =	(2501*xsat_twb -tdb - 2501*x - 1.805 * tdb * x ) / (2.381 * xsat_twb - 4.186 * x - 1 )
Patm =	1,01325	bar					tdb =	23,0	°C
				xsat_twb =	0,015132	kg/kg
Saturation pressure of water at wet bulb temperature					x =	0,013046	kg/kg
Input					twb =	17,99
twb =	23,89	°C
Psat =(1/100)* Exp(ca / tK + cb + cc * tK + cd * tK ^ 2 + ce * tK ^ 3 + cf * Ln(tK)) [bar]

tK =	t + 273.15	°C
tK =	297,038888888889	K
ca =	-5800,22006
cb =	-5,516256
cc =	-0,048640239
cd =	4,17648E-05
ce =	-1,44521E-08
cf =	6,5459673

Psat_wb =	0,02965	bar

## 57.- fi(tdb,ent,H)
				Rev.cjc.29,06,2017

57.- Relative humidity f = f(tdb, ent, H)

Input data				Relative humidity		[1], Eq. (8b)
tdb =	24,0	°C		f = (Patm/Psat) * (x /(0.62198 + x ) )
ent =	71,0	kg/kg		Patm =	1,01325	bar
H =	550	m		Psat =	0,02985	bar
				x =	0,01848	kg/kg
Absolute humidity		[1], Eq. (32b)		f =	0,980	-
x =	(ent - tdb) / (2501 + 1.805*tdb )
ent =	71,0	kg/kg
tdb =	24,0	ºC		Using the function 57
x =	0,018485	kg/kg		f =	Sicro_Relative_Humidity_tdb_ent_H(tdb, ent, H)
				tdb =	24,0	°C
Atmospheric pressure		[1], Eq. (3)		ent 0	71,0	kg/kg
Patm= 1.01325 * (1-0.0000225577 *H) ^ 5.25588				H =	550	m
H =	0,0	m		f =	91,7	%
Patm =	1,01325	bar

Saturation pressure at dry bulb temperature
		[2]
Psat=Sicro_Saturated_vapor_pressure_t(tdb *0.00001
tdb =	24,0	|C
Psat =	0,02985	bar

## Air_Water_props
				Rev.cjc.29,06,2017

Saturated water properties				0 ºC <= t <= 100 ºC

Input data: Temperature			t =	22	ºC

Function				Results
SaturatedWaterConductivity_t			k =	0,606	W/(m*K)
SaturatedWaterSpecificHeat_t			Cp =	4,18	kJ/(kg*K)
SaturatedWaterPrandtl_t			Pr =	6,60	-
SaturatedWaterDensity_t			r =	998,0	kg/m3
SaturatedWaterAbsoluteViscosity_t			m =	9,56E-04	Pa*s
SaturatedWaterKinematicViscosity_t			n =	9,58E-07	m2/s
SaturatedWaterThermalDiffusivity_t			a =	1,45E-04	m2/s

Atmospheric Dry air properties					-73.15b ºC <= t <= 726.85 ºC
				Pressurized dry air properties
Input data: Temperature			t =	45	ºC
				P =	234	kPa
Function				Results			t =	56	ºC
AirConductivity_t			k =	0,028	W/(m*K)
AirSpecificHeat_t			Cp =	1,01	kJ/(kg*K)		r =	Density_Press_Air_PkPa_tCelcius
AirPrandtl_t			Pr =	0,70	-		r =	2,40	kg/m3
AirDensity_t			r =	1,101	kg/m3
AirAbsoluteViscosity			m =	1,93E-05	Pa*s		n =	KinemViscPress_PkPa_tCelcius
AirKinematicViscosity_t			n =	1,75E-05	m2/s		n =	8,28E-06	m2/s
AirThermalDiffusivity_t			a =	2,49E-05	m2/s