## Ref1
OpenOffice, IF-97 Steam tables.					OpenOffice, IF-97 Steam tables. By: Magnus Holmgren
By: Magnus Holmgren

## Added functions
'___________________________________________________________________________________________________________
'
' 7. Added functions (approximated values are used in some cases) Rev. cjc 27.03.2117
'____________________________________________________________________________________________________________

'7.1.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and t					P =	1	bar
					T =	100	ºC		'7.1.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and t
Function ny_pt(p, t)
					H2O_DynViscosity_t_p(t,p)		my_p,T =	1,23E-05	Pa s		Function ny_pt(p, t)
ny_pt = my_pT(p, t) / rho_pT(p, t)
					RHO_PT		rho_pT =	0,59	kg/m³		ny_pt = my_pT(p, t) / rho_pT(p, t)
End Function
					H2O_KinemViscosity_t_p(t,p)		ny_pT =	my_p,T / rho_pT			End Function
					ny_pT =	2,08E-05	m²/s
					Function:		ny_pT =	2,08E-05	m²/s

'7.2.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and h					P =	1	bar		'7.2.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and h
					T =	100	ºC
Function ny_ph(p, h)					Function ny_ph(p, h)
					H2O_Enthalpy_t_p(t,p)		h_p,T =	2675,77	kJ/kg
ny_ph = my_ph(p, h) / rho_ph(p, h)					ny_ph = my_ph(p, h) / rho_ph(p, h)
					P =	1	bar
End Function					h =	2675,77	kJ/kg		End Function

					my_ph =	1,23E-05	Pa s
					rho_ph =	0,59

					ny_ph =	my_ph / rho_ph
					ny_ph =	2,08E-05	m²/s
					Function:		ny_ph =	2,08E-05	m²/s

'7.3.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and s					P =	1	bar		'7.3.- Kinematic viscosity of superheated steam or subcooled liquid as function of p and s
					T =	100	ºC
Function ny_ps(p, s)					Function ny_ps(p, s)
					H2O_Entropy_t_p(t,p)		s_pT =	7,36	kJ/(kg K)
ny_ps = my_ps(p, s) / rho_ps(p, s)					ny_ps = my_ps(p, s) / rho_ps(p, s)
					P =	1	bar
End Function					s =	7,36	kJ/kg		End Function

					my_ps =	1,23E-05	Pa s
					rho_ps =	0,59
					ny_ps =	my_ps / rho_ps
					ny_ps =	2,08E-05	m²/s
					Function:		ny_ps =	2,08E-05	m²/s

'7.4.- Dynamic viscosity of saturated liquid as function of the pressure					P =	1	bar
					'7.4.- Dynamic viscosity of saturated liquid as function of the pressure
Function myL_P(p)					Tsat_p(p) =	99,61
					Tsat_p(p) -0,1 =	99,51			Function myL_P(p)
myL_P = my_pT(p, (Tsat_p(p) - 0.1))
					myL_P =	my_pT(p; (Tsat_p(p) - 0.1))			myL_P = my_pT(p, (Tsat_p(p) - 0.1))
End Function					myL_P =	2,83E-04	Pa s
					End Functio
					Function:		myL_P(p) =	myL_P(p)
					myL_P(p) =	2,83E-04

'7.5.- Dynamic viscosity of saturated liquid as function of the temperature					T =	99,61	ºC
					'7.5.- Dynamic viscosity of saturated liquid as function of the temperature
Function myL_t(t)
					Function myL_t(t)
myL_t = my_pT((psat_T(t) + 0.1), t)
					myL_t = my_pT((psat_T(t) + 0.1), t)
End Function					myL_t(t)	myL_t(t)
					Function:		myL_t(t)	2,83E-04	Pa s		End Function

'7.6.- Dynamic viscosity of saturated vapor as function of the pressure					P =	1	bar
Function myV_P(p)					'7.6.- Dynamic viscosity of saturated vapor as function of the pressure
					Function myV_P(p)
myV_P = my_pT(p, (Tsat_p(p) + 0.1))
					myV_P = my_pT(p, (Tsat_p(p) + 0.1))
End Function					myV_P(p)	myV_P(p)
					Function:		myV_P(p)	1,23E-05	Pa s		End Function

'7.7.- Dynamic viscosity of saturated vapor as function of the temperature					T =	99,61	ºC
					'7.7.- Dynamic viscosity of saturated vapor as function of the temperature
Function myV_t(t)
					Function myV_t(t)
myV_t = my_pT((psat_T(t) - 0.1), t)
					myV_t = my_pT((psat_T(t) - 0.1), t)
End Function					myV_t(t)	myV_t(t)
					myV_t(t)	1,23E-05	Pa s		End Function

'7.8.- Kinematic viscosity of saturated liquid as function of the pressure					P =	1	bar
					'7.8.- Kinematic viscosity of saturated liquid as function of the pressure
Function nyL_P(p)
					Function nyL_P(p)
nyL_P = my_pT(p, (Tsat_p(p) - 0.1)) / rhoL_p(p)
					nyL_P = my_pT(p, (Tsat_p(p) - 0.1)) / rhoL_p(p)
End Function					nyL_P(p)	nyL_P(p)
					nyL_P(p)	2,95E-07	m²/s		End Function

'7.9.- Kinematic viscosity of saturated liquid as function of the temperature					T =	99,61	ºC
Function nyL_t(t)					'7.9.- Kinematic viscosity of saturated liquid as function of the temperature
					Function nyL_t(t)
nyL_t = myL_t(t) / rhoL_T(t)
					nyL_t = myL_t(t) / rhoL_T(t)
End Function					nyL_t(t)	nyL_t(t)
					nyL_t(t)	2,95E-07	m²/s		End Function

'7.10.- Kinematic viscosity of saturated vapor as function of the pressure					P =	1	bar
					'7.10.- Kinematic viscosity of saturated vapor as function of the pressure
Function nyV_P(p)
					Function nyV_P(p)
nyV_P = my_pT(p, (Tsat_p(p) + 0.1)) / rhoV_p(p)
					nyV_P = my_pT(p, (Tsat_p(p) + 0.1)) / rhoV_p(p)
End Function					nyV_P(p)	nyV_P(p)
					nyV_P(p)	2,08E-05	m²/s		End Function

'7.11.- Kinematic viscosity of saturated vapor as function of the temperature					T =	99,61	ºC
Function nyV_t(t)					'7.11.- Kinematic viscosity of saturated vapor as function of the temperature

nyV_t = my_pT((psat_T(t) - 0.1), t) / rhoV_p(psat_T(t) )					Function nyV_t(t)

End Function					nyV_t = my_pT((psat_T(t) - 0.1), t) / rhoV_p(psat_T(t) )
					nyV_t(t)	nyV_t(t)
					nyV_t(t)	2,08E-05	m²/s		End Function

'7.12.- Prandtl number of saturated liquid as function of the pressure					P =	1	bar
Function PrL_P(p)					'7.12.- Prandtl number of saturated liquid as function of the pressure
					Function PrL_P(p)
PrL_P = Pr_pT(p, (Tsat_p(p) - 0.1))
					PrL_P = Pr_pT(p, (Tsat_p(p) - 0.1))
End Function					PrL_P(p)	PrL_P(p)
					PrL_P(p)	1,76	-		End Function

'7.13.- Prandtl number of saturated liquid as function of the temperature					T =	99,61	ºC
					'7.13.- Prandtl number of saturated liquid as function of the temperature
Function PrL_t(t)
					Function PrL_t(t)
PrL_t = Pr_pT((psat_T(t) + 0.1), t)
					PrL_t = Pr_pT((psat_T(t) + 0.1), t)
End Function					PrL_t(t)	PrL_t(t)
					PrL_t(t)	1,76	-		End Function

'7.14.- Prandtl number of saturated vapor as function of the pressure
					P =	1	bar		'7.14.- Prandtl number of saturated vapor as function of the pressure
Function PrV_P(p)
					Function PrV_P(p)
PrV_P = Pr_pT(p, (Tsat_p(p) + 0.1))
					PrV_P = Pr_pT(p, (Tsat_p(p) + 0.1))
End Function					PrV_P(p)	PrV_P(p)
					PrV_P(p)	1,03	-		End Function

'7.15.- Prandtl number of saturated vapor as function of the temperature					T =	99,61	ºC
					'7.15.- Prandtl number of saturated vapor as function of the temperature
Function PrV_t(t)
					Function PrV_t(t)
PrV_t = Pr_pT((psat_T(t) - 0.1), t)
					PrV_t = Pr_pT((psat_T(t) - 0.1), t)
End Function					PrV_t(t)	PrV_t(t)
					PrV_t(t)	1,02			End Function

'7.16.- Specific volume in the humid region as function of pressure and dryness					P =	10	bar
					X =	0,8	-		'7.16.- Specific volume in the humid region as function of pressure and dryness
Function v_px(p, X)
					Function v_px(p, X)
v_px = vL_p(p) + X * (vV_p(p) - vL_p(p))
					v_px = vL_p(p) + X * (vV_p(p) - vL_p(p))
End Function					v_px(p, X)	v_px(p, X)
					v_px(p, X)	0,16	m3/kg		End Function

'7.17.- Specific volume in the humid region as function of temperature and dryness					T =	179,89	ºC
					X =	0,8	-		'7.17.- Specific volume in the humid region as function of temperature and dryness
Function v_tx(t, X)
					Function v_tx(t, X)
v_tx = vL_T(t) + X * (vV_T(t) - vL_T(t))
					v_tx = vL_T(t) + X * (vV_T(t) - vL_T(t))
End Function					v_tx(t, X)	v_tx(t, X)
					v_tx(t, X)	0,16			End Function

'7.18.- Vapourisation Heat as a function of the pressure					P =	10	bar
					'7.18.- Vapourisation Heat as a function of the pressure
Function hfg_p(p)
					Function hfg_p(p)
hfg_p = hV_p(p) - hL_p(p)
					hfg_p = hV_p(p) - hL_p(p)
End Function					hfg_p(p)	hfg_p(p)
					hfg_p(p)	2014,44	kJ/kg		End Function

'7.19.- Vapourisation Heat as a function of the temperature

Function hfg_t(t)					T =	179,89	ºC
					'7.19.- Vapourisation Heat as a function of the temperature
hfg_t = hV_T(t) - hL_T(t)
					Function hfg_t(t)
End Function
					hfg_t = hV_T(t) - hL_T(t)
					hfg_t(t)	hfg_t(t)
					hfg_t(t)	2014,42			End Function

'7.20.- Dryness in the humid region as function of temperature and entropy					P =	10	bar
					X =	0,8	-		'7.20.- Dryness in the humid region as function of temperature and entropy
Function x_ts(t, s)					Tsat_p =	179,89	ºC
					h_px =	2374,2	kJ/kg		Function x_ts(t, s)
x_ts = (s - sL_T(t)) / (sV_T(t) - sL_T(t))					s_pH =	5,7	kJ/(kg K)
					x_ts = (s - sL_T(t)) / (sV_T(t) - sL_T(t))
End Function					x_ts(t, s)	x_ts(t, s)
					x_ts(t, s)	0,8			End Function

'========================================================

## Example.xls
Desuperheater
Example 15.1.1		[2]

Water at a state (Pw, tw) is injected into a steam flow at a state (Ps, ts) , in an isobaric process (at Ps),
to a temperature slightly above the saturation temperature (tsat at Ps). For example, some 5 K above it (state rs).

Steam supply				Ps =	10	kPa		Thermal balance
Ps =	10	bar		ts =	300	ºC		Hs + Hw =		Hsr
ts =	300	ºC		hs =	h_pt			hs * ms + hw * mw =		(ms + mw)*hrs
ms =	10000	kg/h		hs =	3052	kJ/kg		( hs - hrs)* ms =		mw * (hrs -hw)
				tsat_ps =	180	ºC		mw =	( hs - hrst)* ms / (hrs -hw)

Cooling water supply				Pw =	15	bar		Water mass flow rate
Pw =	15	bar		tw =	150	ºC		hs =	3052	kJ/kg
tw =	150	ºC		hw =	h_pt			hrs =	2790,4	kJ/kg
				hw =	633	kJ/kg		ms =	2,78	Kg/s
					hw =	632,9	kJ/kg
Required steam confitions				Prs =	10	kPa		mw =	0,34	kg/s
Psr =	10	bar		tsat =	tsat_P			mw =	1211	kg/h
tsr =	5	ºC		tsat =	180	ºC
				tsr =	185	ºC		Total steam supplied
				hrs =	h_pt			mstot =	ms + mw
				hrs =	2790	kJ/kg		ms =	10000	kg/h
					mw =	1211	kg/h
					mstot =	11211	kg/h

## Example.pdf
http://www.spiraxsarco.com/Resources/Pages/Steam-Engineering-Tutorials/desuperheating/basic-desuperheating-theory.aspx

					Steam supply
					Ps =	10	bar
					ts =	300	ºC
					ms =	10.000	kg/h

					Cooling water supply
					pw =	15	bar
					tw =	150	ºC

					Required steam confitions
					Psr =	10	bar
					tsr =	tsat + 5	1C

Desuperheater
Water is injected into a steam flow at a state (Ps, ts) , in an isobaric process, to a temperature slightly above the saturation temperature (example, some 5 K).

Desuperheater
Water is injected into a steam flow at a state (Ps, ts) , in an isobaric process, to a temperature slightly above the saturation temperature (example, some 5 K).

## Steam Properties
Magnus Holmgren

Saturation properties	p =	1	bar	Steamdat	Added		Humid region					Superheated steam	p =	1	bar
		Magnus		(for p = 1 bar)	functions				Magnus		Steamdat				t =	100	ºC	Steamdat	Added
SaturSteam_Entropy_p(p)	sV_p =	7,36	kJ(kg K)	7,36				p =	10	bar	(for p = 1 bar, x = 0.8)					Magnus		(for p = 1 bar, t = 100 ºC)	functions
SaturWater_Entropy_p(p)	sL_p =	1,3	kJ(kg K)	1,3				x =	0,8	-				H2O_Entropy_t_p(t,p)	s_pT =	7,36	kJ/(kg K)	7,36
H2O_SaturationTemp_p(p)	Tsat_p =	99,61	ºC	99,6				Tsat_p =	179,89	ºC	179,89			H2O_Enthalpy_t_p(t,p)	h_pT =	2675,77	kJ/kg	2675,8
SaturWater_Enthalpy_t(t)	hL_p =	417,44	kJ/kg	417,4					H2O_SpecVolume_p_h(t,p)	v_pT =	1,7	m3/kg	1,7
					H2O_Enthalpy_p_x(p,x)	h_px =	2374,2	kJ/kg	2374,2
Saturated water					H2O_Enthalpy_t_x(t,x)	h_Tx =	2374,2	kJ/kg	2374,2			H2O_DynViscosity_t_p(t,p)	my_pT =	1,23E-05	Pa s	1,23E-05
H2O_SaturationPressure_s(s)	-		bar	1			H2O_Entropy_p_h(p,h)	s_pH =	5,7	kJ/(kg K)	5,7				my_ph =	1,23E-05	Pa s
H2O_SaturationPressure_t(t)	psat_T =	1	bar	1			H2O_SpecVolume_p_x(p,x)	v_px =	0,16	m³/kg	0,1557	7.16			my_ps =	1,23E-05	Pa s
H2O_SaturationTemp_s(s)	-		ºC	99,6			H2O_SpecVolume_t_x(t,x)	v_tx =	0,16	m³/kg	0,1557	7,17		H2O_KinemViscosity_t_p(t,p)	ny_pT =	2,08E-05	m²/s		7,1
SaturWater_DynViscosity_t(t)	-		Pa s	2,80E-04			SteamQuality_p_h(p,h)	x_ph =	0,8	-	0,8				ny_ph =	2,08E-05	m²/s		7,2
SaturWater_Enthalpy_p(p)	hL_p =	417,44	kJ/kg	417			SteamQuality_p_s(p,s)	x_ps =	0,8	-	0,8				ny_ps =	2,08E-05	m²/s		7,3
SaturWater_Enthalpy_t(t)	hL_t =	417,44	kJ/kg	417			SteamQuality_t_s(t,s)	x_ts =	0,8	-	0,8	7.20		H2O_Enthalpy_p_s(p,s)	h_ps =	2675,8	kJ/kg	2675,8
SaturWater_Entropy_p(p)	sL_P =	1,3	kJ(kg K)	1,3			H2O_VapourisationHeat_p(p)	hfg_p =	2014,44	kJ/kg	2014,4	7.18		H2O_Enthalpy_t_p(t,p)	h_pt =	2675,8	kJ/kg	2675,8
SaturWater_Entropy_t(t)	sL_t =	1,3	kJ(kg K)	1,3			H2O_VapourisationHeat_t(t)	hfg_t =	2014,44	kJ/kg	2014,4	7.19		H2O_Enthalpy_t_s(t,s)			kJ/kg	2675,8
SaturWater_HeatConduct_t(t)	tcL_t =	0,68	W/(m K)	0,68					h_prho =	2675,8	kJ/kg
SaturWater_Prandtl_p(p)	PrL_P =	1,76	-	1,76	7.12					H2O_Entropy_p_h(p,h)	s_ph =	7,36	kJ/(kg K)	7,36
SaturWater_Prandtl_t(t)	PrL_t =	1,76	-		7.13					H2O_Entropy_t_p(t,p)	s_pt =	7,36	kJ/(kg K)	7,36
SaturWater_SonicVelocity_t(t)	wL_t =	1545,45	m/s	1545,5					H2O_HeatConductivity_t_p(t,p)	tc_pt =	0,0248	W/(m K)	0,0251
	wL_p =	1545,45	m/s					tc_ph =	0,0248	W/(m K)
SaturWater_SpecHeat_Cp_t(t)	CpL_p =	4,22	kJ/(kg K)	4,22					tc_hs =	0,0248	W/(m K)
	CpL_t =	4,22	kJ/(kg K)					H2O_Kappa_p_h(p,h)			-	1,32
SaturWater_SpecVolume_t(t)	vL_T =	0,00104	m³/kg	0,00104					H2O_KappaUp_p_h(p,h)			-	1,32
	vL_p =	0,00104	m³/kg					H2O_KappaDown_p_h(p,h)			-	1,32
SaturWater_Temperature_h(h)	-		ºC	99,6				P =	10	bar				H2O_Prandtl_t_p(t,p)	Pr_pT =	1,027	-	1,015
Water_SurfaceTension_t(t)	st_T =	0,059	N/m	0,059				x =	0,8					Pr_ph =	1,027
	st_p =	0,06	N/m					Tsat =	179,89					H2O_Pressure_t_s(t,s)			bar	1
	rhoL_T	958,64	kg/m³					vg =	0,1943	m³/kg				H2O_Pressure_t_v(t,v)			bar	1
	rhoL_p	958,64	kg/m³					vf =	0,0011	m³/kg					p_hs	1	bar
	uL_T =	417,33	kJ/kg					p_hrho	1	bar
	uL_p =	417,33	kJ/kg					v =	vf + x*(vg – vf)					H2O_SonicVelocity_p_h(p,h)	w_ph =	472,3	m/s	472,3
SaturWater_DynViscosity_p(p)	myL_P =	2,83E-04	Pa s		7.4			vf =	0,0011	m³/kg				H2O_SonicVelocity_t_p(t,p)	w_pT =	472,3	m/s	472,3
SaturWater_DynViscosity_t(t)	myL_t =	2,83E-04	Pa s		7.5			x =	0,8	-					w_ps =	472,3
SaturWater_KinemViscosity_t(t)	nyL_P =	2,95E-07	m²/s		7.8			vg =	0,1943	m³/kg				H2O_SpecificHeat_Cp_t_p(t,p)	Cp_pT =	2,07	kJ/(kg K)	2,07
SaturWater_KinemViscosity_p(p)	nyL_t =	2,95E-07	m²/s		7.9			v =	0,1557	m³/kg					Cp_ph =	2,07	kJ/(kg K)
					Cp_ps =	2,07	kJ/(kg K)
					H2O_SpecificHeat_Cv_t_p(t,p)	Cv_pT =	1,551	kJ/(kg K)	1,551
					Cv_ph =	1,55	kJ/(kg K)
					Cv_ps =	1,55	kJ/(kg K)
					H2O_SpecVolume_p_h(t,p)	v_pT =	1,696	kJ/(kg K)	1,696
					H2O_SpecVolume_p_h(p,h)	v_ph =	1,696	kJ/(kg K)	1,696
Saturated steam					v_ps =	1,696	kJ/(kg K)
SaturSteam_DynViscosity_t(t)	-	-	Pa s	1,20E-05
SaturSteam_Enthalpy_p(p)	hV_p =	2675	kJ/kg	2675					H2O_Temperature_p_h(p,h)	T_ph =	100	ºC	100
SaturSteam_Enthalpy_t(t)	hV_T =	2675	kJ/kg	2675					H2O_Temperature_p_s(p,s)	T_ps =	100	ºC	100
SaturSteam_Entropy_p(p)	sV_p =	7,36	kJ/(kg K)	7,36					H2O_Temperature_p_v(p,v)			ºC	100
SaturSteam_Entropy_t(t)	sV_t =	7,36	kJ/(kg K)	7,36					T_hs =	100	ºC
SaturSteam_HeatConduct_t(t)	tcV_t =	0,025	W/(m K)	0,025					rho_pT =	0,59	kg/m³
SaturSteam_Prandtl_p(p)	PrV_p =	1,03	-	1,02	7,14					rho_ph =	0,59	kg/m³
SaturSteam_Prandtl_t(t)	PrV_t =	1,02			7,15					rho_ps =	0,59	kg/m³
SaturSteam_SonicVelocity_t(t)	wV_T =	472	m/s	472					u_pT =	2506,17	kJ/kg
	wV_p =	472	m/s					u_ph =	2506,18	kJ/kg
SaturSteam_SpecHeat_Cp_t(t)	CpV_T =	2,08	kJ/(kg K)	2,08					u_ps =	2506,18	kJ/kg
	CpV_p =	2,08	kJ/(kg K)
SaturSteam_SpecVolume_t(t)	vV_T =	1,69	m3/kg	1,69
	vV_T =	1,69	m3/kg
SaturSteam_Density	rhoV_T =	0,59	kg/m³
	rhoV_p =	0,59	kg/m³
SaturSpecificEnergy	uV_p =	2505,55	kJ/kg
	uV_T =	2505,55	kJ/kg
SaturVapor_DynViscosity_p(p)	myV_P =	1,23E-05	Pa s		7.6
SaturVapor_DynViscosity_t(t)	myV_t =	1,23E-05	Pa s		7.7
SaturVapor_KinemViscosity_t(t)	nyV_P =	2,08E-05	m²/s		7.1
SaturVapor_KinemViscosity_p(p)	nyVt =	2,08E-05	m²/s		7.11

Approximated value of saturated viscosity
	P =	1	bar
Saturation liquid viscosity(p)	mySatL_p =	2,83E-04	Pa s
Saturation Vapor viscosity(p)	mySatV_p =	1,23E-05	Pa s

These viscosity values allow the Prandtl number to be estimated					Steamdat
					for P = 1 bar
PrSatL_P =	1000* CPL_P(p) * MY_PT(p,(TSAT_P(p)-0.01)) / TCL_T( TSAT_P(p))
PrSatL_P =	1,761					1,760

PrSatV_P =	1000*CPV_P(p) * MY_PT(p,(TSAT_P(p)+0.01)) / TCV_T(TSAT_P(p))
PrSatV_P =	1,028	-					1,015

## Ref
[1]	Water and steam properties according to IAPWS IF-97
	By Magnus Holmgren, www.x-eng.com
	The steam tables are free and provided as is.
	We take no responsibilities for any errors in the code or damage thereby.
	You are free to use, modify and distribute the code as long as authorship is properly acknowledged.
	Please notify me at magnus@x-eng.com if the code is used in commercial applications

[2]	http://www.spiraxsarco.com/Resources/Pages/Steam-Engineering-Tutorials/desuperheating/basic-desuperheating-theory.aspx