## Sand trap
Sand Trap
Volume flow rate |  |  | The sand trap shall provide enough residence time to allow the particles |  |  |  |  | Particle settlig velocity
Q = | 500 | m3/h | with diameters larger than a given diameter "d" ,to travel down a vertical |  |  |  |  | d = | 0.015 | mm
Sand trap dimensions |  |  | distance "H", larger than the depth "ho" at the discharge. |  |  |  |  | rs = | 2400 | kg/m3
b = | 5 | m | [5 empty] | rL = | 1000 | kg/m3
h = | 5 | m |  | Particle diameter | d = | 15 | mm | m = | 0.001 | Pa s
L = | 6 | m |  | Particle density | rs = | 2400 | kg/m3 | vy = | Pipe_Slurry_Vel_Decantacion_d_rs_rL_m(P7, P8, P9, P10)
|  |  |  | Liquid density | rL = | 1000 | kg/m3 | vy = | 0.00018216 | m/s
Depth ho of outlet channel for |  |  |  | Liquid voscosity | m = | 0.001 | Pa s
a water velocity of | [7 empty] | Peaking of the particle (H) in the time interval
vout = | 2 | m/s |  |  | Sand trap flow section |  |  | (down travel distance)
with an assumed channel width |  |  |  |  | A = | b * h |  | H = | vy * t
bch = | 800 | mm |  |  | b = | 5 | m | vy = | 0.00018216 | m/s
Resulting depth |  |  |  |  | h = | 5 | m | t = | 1080
ho = | Q / (vout * bch) |  |  |  | A = | 25 | m2 | H = | 0.19673 | m
Q = | 0.13889 | m3/s | [5 empty] | H = | 196.7317 | mm
vout = | 2 | m |  |  | Particle horizontal velocity vx (Note 1) |  |  |  | H > ho. Correct |  | Water surface
bch = | 0.8 | m |  |  | v = | Q / A
ho = | 0.086806 | m |  |  | Q = | 0.13889
ho = | 86.8056 | mm |  |  | A = | 25
[5 empty] | vx = | 0.0055556 | m/s
Residence time of particles
[5 empty] | t = | L/v
Note 1. In this calculation, the horizontal particle velocity has been assumed |  |  |  |  | L = | 6 | m
to be equal to water flow velocity, although the real horizontal particle velocity |  |  |  |  | vx = | 0.0055556 | m/s
is smaller than the flow velocity. Thus, the real residence time is larger than |  |  |  |  | t = | 1080 | s
the calculated value. | [10 empty] | cjc | 17.01.10
H
L
b
h
vx
vy
ho
Q
Q

## Settling velocity
Settling velocity
Settling velocity of a sphere of diameter "d" [mm], of a material with density "rs" |  | v = | Pipe_Slurry_Vel_Decantacion_d_rs_rL_m(d, rs, rL, m)
in a fluid with density "rL" and absolute voscosity "m" [Pa*s] |  | d = | 2 | mm
|  | rs = | 2400 | kg/m3
|  | rL = | 1000 | kg/m3
|  | m = | 0.001 | Pa s
|  | v = | 0.2552 | m/s
|  | d | d | v | v
v = | ((4 *g *d *(rs - rL) / (3 * CD * rL))^0.5 | mm | mm | m/s | m/s | mm/s
v = | ((4 *g *d *(rs - rL) / (3 * (Pipe_Slurry_DragCoefficient_CD_Re(Re)) * rL))^0.5 | 10 | 0.01 |  | 8.6823e-05 | 0.00086823
|  | 50 | 0.05 |  | 0.0017076 | 0.017076
Re = | v * d * r / m | 200 | 0.2 |  | 0.018839 | 0.18839
CD = | (Pipe_Slurry_DragCoefficient_CD_Re(Re)) | 500 | 0.5 | 0.063 | 0.063222 | 0.63222
|  | 1000 | 1 | 0.1365 | 0.13655 | 1.3655
The function is valid for resultin Reynolds numbers within the range |  | 2000 | 2 | 0.255 | 0.2552 | 2.552
| 0.0002 < Re < 1.000.000 | 3000 | 3 | 0.361 | 0.3609 | 3.609
This limits are given due to the validity range of the graphic CD = CD(Re) |  | 4000 | 4 | 0.42 | 0.42044 | 4.2044
|  | 5000 | 5 | 0.473 | 0.47332 | 4.7332
|  | 6000 | 6 | 0.521 | 0.52142 | 5.2142
[7 empty] | cjc | 17.01.10

## Ref
Wasp, Edward J.
Solid - Liquid flow Slurry pipeline transportation
1978